## 00_Scope
metric | value
source_tags | 603
live_tags | 603
searchable_tags | 606
model_source_raw_observed_tags | 3
rules | 55
live_rules | 53
source_mapped_rules | 3
input_groups | 37
live_input_groups | 35
equipment_pages | 9
pages | 102
native_inputs | 47
native_outputs | 30
derived_outputs | 28

## 01_All_Current_Logic
rule_id | group | logic_name | logic_type | input_nodes | condition | delay | reset_hysteresis | output_nodes_or_tags | output_class | input_group_id | validation_status | source_basis | source_kind | source_mapped | runtime_inclusion | model_source_status | raw_session_status | raw_rows | raw_closed_samples | raw_open_samples | open_behavior_test_status
AL-GT-FLOW-L | GT Exhaust | GT exhaust flow low | ALARM | vppGTExhaustMassFlowState | value < 545 kg/s | 0.2 s | +6 kg/s | GT.EXHAUST.FLOW.L | DERIVED_ALARM | IG-001 | PARTIAL | Current DCS alarm rule; RAW input node exists | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-GT-FLOW-LL | GT Exhaust | GT exhaust flow low-low | ALARM | vppGTExhaustMassFlowState | value < 300 kg/s | 0.2 s | +6 kg/s | GT.EXHAUST.FLOW.LL | DERIVED_ALARM | IG-001 | PARTIAL | Current DCS alarm rule; RAW input node exists | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-GT-TEMP-L | GT Exhaust | GT exhaust temperature low | ALARM | vppGTExhaustTemperatureK | value < 805 K | 0.2 s | +5 K | GT.EXHAUST.TEMP.L | DERIVED_ALARM | IG-002 | PARTIAL | Current DCS alarm rule; RAW input node exists | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-GT-TEMP-LL | GT Exhaust | GT exhaust temperature low-low | ALARM | vppGTExhaustTemperatureK | value < 580 K | 0.2 s | +5 K | GT.EXHAUST.TEMP.LL | DERIVED_ALARM | IG-002 | PARTIAL | Current DCS alarm rule; RAW input node exists | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-HP-FLOW-L | HP Steam Flow | HP turbine steam flow L | ALARM | vppHPTurbineSteamFlowTH | value < 486 t/h | 0.2 s | 10.8 t/h | HRSG.HP.STEAM.FLOW.L | DERIVED_ALARM | IG-005 | PARTIAL | Current DCS alarm rule; RAW node is vpp*TurbineSteamFlowTH; threshold converted exactly from kg/s × 3.6 | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-HP-FLOW-LL | HP Steam Flow | HP turbine steam flow LL | ALARM | vppHPTurbineSteamFlowTH | value < 324 t/h | 0.2 s | 10.8 t/h | HRSG.HP.STEAM.FLOW.LL | DERIVED_ALARM | IG-005 | PARTIAL | Current DCS alarm rule; RAW node is vpp*TurbineSteamFlowTH; threshold converted exactly from kg/s × 3.6 | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-HP-LEVEL-H | HP Drum | HP drum level H | ALARM | vppHPDrumLevelM | value > 1.15 m | 0.5 s | 0.02 m | HRSG.HP.DRUM.LEVEL.H | DERIVED_ALARM | IG-003 | PARTIAL | Current DCS alarm rule; RAW input node exists | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-HP-LEVEL-HH | HP Drum | HP drum level HH | ALARM | vppHPDrumLevelM | value > 1.25 m | 0.5 s | 0.02 m | HRSG.HP.DRUM.LEVEL.HH | DERIVED_ALARM | IG-003 | PARTIAL | Current DCS alarm rule; RAW input node exists | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-HP-LEVEL-L | HP Drum | HP drum level L | ALARM | vppHPDrumLevelM | value < 0.95 m | 0.5 s | 0.02 m | HRSG.HP.DRUM.LEVEL.L | DERIVED_ALARM | IG-003 | PARTIAL | Current DCS alarm rule; RAW input node exists | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-HP-LEVEL-LL | HP Drum | HP drum level LL | ALARM | vppHPDrumLevelM | value < 0.85 m | 0.5 s | 0.02 m | HRSG.HP.DRUM.LEVEL.LL | DERIVED_ALARM | IG-003 | PARTIAL | Current DCS alarm rule; RAW input node exists | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-HP-PRESS-L | HP Drum | HP drum pressure L | ALARM | vppHPDrumPressurePa | value < 12000000 Pa | 0.5 s | 200000 Pa | HRSG.HP.DRUM.PRESS.L | DERIVED_ALARM | IG-004 | PARTIAL | Current DCS alarm rule; RAW input node exists | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-HP-PRESS-LL | HP Drum | HP drum pressure LL | ALARM | vppHPDrumPressurePa | value < 10800000 Pa | 0.5 s | 200000 Pa | HRSG.HP.DRUM.PRESS.LL | DERIVED_ALARM | IG-004 | PARTIAL | Current DCS alarm rule; RAW input node exists | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-IP-FLOW-L | IP Steam Flow | IP turbine steam flow L | ALARM | vppIPTurbineSteamFlowTH | value < 576 t/h | 0.2 s | 10.8 t/h | HRSG.IP.STEAM.FLOW.L | DERIVED_ALARM | IG-008 | PARTIAL | Current DCS alarm rule; RAW node is vpp*TurbineSteamFlowTH; threshold converted exactly from kg/s × 3.6 | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-IP-FLOW-LL | IP Steam Flow | IP turbine steam flow LL | ALARM | vppIPTurbineSteamFlowTH | value < 378 t/h | 0.2 s | 10.8 t/h | HRSG.IP.STEAM.FLOW.LL | DERIVED_ALARM | IG-008 | PARTIAL | Current DCS alarm rule; RAW node is vpp*TurbineSteamFlowTH; threshold converted exactly from kg/s × 3.6 | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-IP-LEVEL-H | IP Drum | IP drum level H | ALARM | vppIPDrumLevelM | value > 1.15 m | 0.5 s | 0.02 m | HRSG.IP.DRUM.LEVEL.H | DERIVED_ALARM | IG-006 | PARTIAL | Current DCS alarm rule; RAW input node exists | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-IP-LEVEL-HH | IP Drum | IP drum level HH | ALARM | vppIPDrumLevelM | value > 1.25 m | 0.5 s | 0.02 m | HRSG.IP.DRUM.LEVEL.HH | DERIVED_ALARM | IG-006 | PARTIAL | Current DCS alarm rule; RAW input node exists | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-IP-LEVEL-L | IP Drum | IP drum level L | ALARM | vppIPDrumLevelM | value < 0.95 m | 0.5 s | 0.02 m | HRSG.IP.DRUM.LEVEL.L | DERIVED_ALARM | IG-006 | PARTIAL | Current DCS alarm rule; RAW input node exists | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-IP-LEVEL-LL | IP Drum | IP drum level LL | ALARM | vppIPDrumLevelM | value < 0.85 m | 0.5 s | 0.02 m | HRSG.IP.DRUM.LEVEL.LL | DERIVED_ALARM | IG-006 | PARTIAL | Current DCS alarm rule; RAW input node exists | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-IP-PRESS-L | IP Drum | IP drum pressure L | ALARM | vppIPDrumPressurePa | value < 2550000 Pa | 0.5 s | 50000 Pa | HRSG.IP.DRUM.PRESS.L | DERIVED_ALARM | IG-007 | PARTIAL | Current DCS alarm rule; RAW input node exists | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-IP-PRESS-LL | IP Drum | IP drum pressure LL | ALARM | vppIPDrumPressurePa | value < 2300000 Pa | 0.5 s | 50000 Pa | HRSG.IP.DRUM.PRESS.LL | DERIVED_ALARM | IG-007 | PARTIAL | Current DCS alarm rule; RAW input node exists | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-LP-FLOW-L | LP Steam Flow | LP turbine steam flow L | ALARM | vppLPTurbineSteamFlowTH | value < 630 t/h | 0.2 s | 10.8 t/h | HRSG.LP.STEAM.FLOW.L | DERIVED_ALARM | IG-011 | PARTIAL | Current DCS alarm rule; RAW node is vpp*TurbineSteamFlowTH; threshold converted exactly from kg/s × 3.6 | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-LP-FLOW-LL | LP Steam Flow | LP turbine steam flow LL | ALARM | vppLPTurbineSteamFlowTH | value < 424.8 t/h | 0.2 s | 10.8 t/h | HRSG.LP.STEAM.FLOW.LL | DERIVED_ALARM | IG-011 | PARTIAL | Current DCS alarm rule; RAW node is vpp*TurbineSteamFlowTH; threshold converted exactly from kg/s × 3.6 | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-LP-LEVEL-H | LP Drum | LP drum level H | ALARM | vppLPDrumLevelM | value > 1.85 m | 0.5 s | 0.02 m | HRSG.LP.DRUM.LEVEL.H | DERIVED_ALARM | IG-009 | PARTIAL | Current DCS alarm rule; RAW input node exists | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-LP-LEVEL-HH | LP Drum | LP drum level HH | ALARM | vppLPDrumLevelM | value > 1.95 m | 0.5 s | 0.02 m | HRSG.LP.DRUM.LEVEL.HH | DERIVED_ALARM | IG-009 | PARTIAL | Current DCS alarm rule; RAW input node exists | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-LP-LEVEL-L | LP Drum | LP drum level L | ALARM | vppLPDrumLevelM | value < 1.65 m | 0.5 s | 0.02 m | HRSG.LP.DRUM.LEVEL.L | DERIVED_ALARM | IG-009 | PARTIAL | Current DCS alarm rule; RAW input node exists | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-LP-LEVEL-LL | LP Drum | LP drum level LL | ALARM | vppLPDrumLevelM | value < 1.55 m | 0.5 s | 0.02 m | HRSG.LP.DRUM.LEVEL.LL | DERIVED_ALARM | IG-009 | PARTIAL | Current DCS alarm rule; RAW input node exists | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-LP-PRESS-L | LP Drum | LP drum pressure L | ALARM | vppLPDrumPressurePa | value < 500000 Pa | 0.5 s | 10000 Pa | HRSG.LP.DRUM.PRESS.L | DERIVED_ALARM | IG-010 | PARTIAL | Current DCS alarm rule; RAW input node exists | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
AL-LP-PRESS-LL | LP Drum | LP drum pressure LL | ALARM | vppLPDrumPressurePa | value < 450000 Pa | 0.5 s | 10000 Pa | HRSG.LP.DRUM.PRESS.LL | DERIVED_ALARM | IG-010 | PARTIAL | Current DCS alarm rule; RAW input node exists | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
CMD-FWP-HP-RESET | FWP HP | HP FWP reset command interface | COMMAND_INTERFACE | vppHPFWPResetPushbuttonNative | operator/test reset PB | external runtime interface | - | vppHPFWPTripLatchNative | RAW_NODE | IG-031 | PARTIAL | Reset node exists in RAW; exact reset sequencing remains runtime-owned | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
CMD-FWP-HP-TRIP | FWP HP | HP FWP trip command interface | COMMAND_INTERFACE | vppHPFWPTripPushbuttonNative | operator/test PB writes trip command through runtime interface | external runtime interface | reset PB | vppHPFWPTripCommandNative ¦ vppHPFWPTripLatchNative ¦ vppVCBA01TripCommandNative | RAW_NODE | IG-030 | PARTIAL | All command/latch/breaker nodes exist in RAW; exact client-side sequencing is not re-invented here | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
CMD-FWP-IP-RESET | FWP IP | IP FWP reset command interface | COMMAND_INTERFACE | vppIPFWPResetPushbuttonNative | operator/test reset PB | external runtime interface | - | vppIPFWPTripLatchNative | RAW_NODE | IG-033 | PARTIAL | Reset node exists in RAW; exact reset sequencing remains runtime-owned | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
CMD-FWP-IP-TRIP | FWP IP | IP FWP trip command interface | COMMAND_INTERFACE | vppIPFWPTripPushbuttonNative | operator/test PB writes trip command through runtime interface | external runtime interface | reset PB | vppIPFWPTripCommandNative ¦ vppIPFWPTripLatchNative ¦ vppVCBB01TripCommandNative | RAW_NODE | IG-032 | PARTIAL | All command/latch/breaker nodes exist in RAW; exact client-side sequencing is not re-invented here | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
CMD-FWP-LP-RESET | FWP LP | LP FWP reset command interface | COMMAND_INTERFACE | vppLPFWPResetPushbuttonNative | operator/test reset PB | external runtime interface | - | vppLPFWPTripLatchNative | RAW_NODE | IG-035 | PARTIAL | Reset node exists in RAW; exact reset sequencing remains runtime-owned | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
CMD-FWP-LP-TRIP | FWP LP | LP FWP trip command interface | COMMAND_INTERFACE | vppLPFWPTripPushbuttonNative | operator/test PB writes trip command through runtime interface | external runtime interface | reset PB | vppLPFWPTripCommandNative ¦ vppLPFWPTripLatchNative ¦ vppVCBA02TripCommandNative | RAW_NODE | IG-034 | PARTIAL | All command/latch/breaker nodes exist in RAW; exact client-side sequencing is not re-invented here | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
PROT-DIRECT-GT | GT Protection | Direct GT trip cause | PROTECTION_CAUSE | vppExternalTripCommandNative | command >= 0.5 | 0 s | reset by GT reset | vppCauseDirectGTTrip | RAW_NODE | IG-012 | PASS | RAW node + runtime regression evidence | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
PROT-DIRECT-ST | ST Protection | Direct ST trip cause | PROTECTION_CAUSE | vppExternalSTTripCommandNative | command >= 0.5 | 0 s | reset by ST reset | vppCauseDirectSTTrip | RAW_NODE | IG-013 | PASS | RAW node + runtime regression evidence | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
PROT-GT-BRK-OPEN | GT Protection | GT breaker open while running cause | PROTECTION_CAUSE | vppECMS52GTClosedCommandNative ¦ vppGTTripLatchInternal | 52GT close command < 0.5 AND GT latch not active | 0 s | state reset | vppCauseGTBreakerOpenWhileRunning | RAW_NODE | IG-014 | PARTIAL | Exact expression recovered from model compile trace | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
PROT-GT-LATCH | GT Protection | GT trip latch | LATCH | vppGTTripRequest ¦ vppGTTripResetNative | request=1 AND reset<0.5 -> latch; reset clears | event-driven | reset input | vppGTTripLatch | RAW_NODE | IG-023 | PASS | Runtime latch node and request/reset nodes exist | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
PROT-GT-REQUEST | GT Protection | GT trip request OR matrix | TRIP_REQUEST | vppCauseDirectGTTrip ¦ vppCauseGTBreakerOpenWhileRunning ¦ vppCauseHPDrumLL ¦ vppCauseIPDrumLL ¦ vppCauseLPDrumLL | OR(all inputs) | 0 s | GT reset | vppGTTripRequest | RAW_NODE | IG-021 | PASS | Exact GT request equation recovered from model compile trace | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
PROT-HP-DRUM-HH | HP Drum Protection | HP drum HH protection cause | PROTECTION_CAUSE | vppHPDrumHHRaw | raw HH state == 1 | runtime-defined | reset/return per runtime | vppCauseHPDrumHH | RAW_NODE | IG-015 | PARTIAL | RAW comparator/cause nodes exist; exact internal debounce retained in runtime | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
PROT-HP-DRUM-LL | HP Drum Protection | HP drum LL protection cause | PROTECTION_CAUSE | vppHPDrumLLRaw | raw LL state == 1 | runtime-defined | reset/return per runtime | vppCauseHPDrumLL | RAW_NODE | IG-016 | PARTIAL | RAW comparator/cause nodes exist; exact internal debounce retained in runtime | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
PROT-IP-DRUM-HH | IP Drum Protection | IP drum HH protection cause | PROTECTION_CAUSE | vppIPDrumHHRaw | raw HH state == 1 | runtime-defined | reset/return per runtime | vppCauseIPDrumHH | RAW_NODE | IG-017 | PARTIAL | RAW comparator/cause nodes exist; exact internal debounce retained in runtime | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
PROT-IP-DRUM-LL | IP Drum Protection | IP drum LL protection cause | PROTECTION_CAUSE | vppIPDrumLLRaw | raw LL state == 1 | runtime-defined | reset/return per runtime | vppCauseIPDrumLL | RAW_NODE | IG-018 | PARTIAL | RAW comparator/cause nodes exist; exact internal debounce retained in runtime | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
PROT-LP-DRUM-HH | LP Drum Protection | LP drum HH protection cause | PROTECTION_CAUSE | vppLPDrumHHRaw | raw HH state == 1 | runtime-defined | reset/return per runtime | vppCauseLPDrumHH | RAW_NODE | IG-019 | PARTIAL | RAW comparator/cause nodes exist; exact internal debounce retained in runtime | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
PROT-LP-DRUM-LL | LP Drum Protection | LP drum LL protection cause | PROTECTION_CAUSE | vppLPDrumLLRaw | raw LL state == 1 | runtime-defined | reset/return per runtime | vppCauseLPDrumLL | RAW_NODE | IG-020 | PARTIAL | RAW comparator/cause nodes exist; exact internal debounce retained in runtime | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
PROT-ST-BRK-OPEN | ST Protection | 52ST breaker open protection cause | PROTECTION_CAUSE | vppECMS52STClosedCommandNative | 52ST close command < 0.5 -> breaker-open cause latch | event-driven | ST reset with active trip causes clear and 52ST command open | vppCauseSTBreakerOpenWhileRunning | RAW_NODE | IG-037 | PASS | TRIPLENS_ST_BREAKER_OPEN_TRIP_V1; 2026-09-26 PlantControlV2 build 104046 runtime proof | MODEL_SOURCE_RAW_OBSERVED | Y | SEARCH_ONLY | MODEL_SOURCE_CONFIRMED | USER_RUNTIME_VERIFIED |  |  |  | RUNTIME_VERIFIED
PROT-ST-LATCH | ST Protection | ST trip latch | LATCH | vppSTTripRequest ¦ vppSTTripResetNative | request=1 AND reset<0.5 -> latch; reset clears | event-driven | reset input | vppSTTripLatchPublished | RAW_NODE | IG-024 | PASS | Runtime latch node and request/reset nodes exist | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
PROT-ST-REQUEST | ST Protection | ST trip request | TRIP_REQUEST | vppGTTripRequest ¦ vppCauseDirectSTTrip ¦ vppCauseSTBreakerOpenWhileRunning ¦ vppCauseHPDrumHH ¦ vppCauseIPDrumHH ¦ vppCauseLPDrumHH | OR(registered ST trip inputs) | 0 s | ST reset | vppSTTripRequest | RAW_NODE | IG-022 | PASS | Current PlantControlV2 ST request equation; cause-count wording retired; 52ST breaker-open cause included. | LIVE_OPCUA_CENSUS | Y | LIVE_RUNTIME
RESP-GT-POWER | GT Response | GT power response after breaker open | PHYSICAL_RESPONSE | vpp52GTClosed | if 52GT not closed then GT generator power = 0 | immediate model relation | - | vppGTGPowerMW | RAW_NODE | IG-029 | PASS | Exact model equation | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
RESP-GT-SPEED | GT Response | GT speed coastdown after breaker open | PHYSICAL_RESPONSE | vpp52GTClosed | if 52GT opens, speed decays from nominal by coastdown model | dynamic | - | vppGTGSpeedRPM | RAW_NODE | IG-029 | PASS | Exact model equation | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
RESP-ST-GRID-POWER | ST Protection | ST grid power response after 52ST opens | PHYSICAL_RESPONSE | vppSTGeneratorPowerMW ¦ vpp52STClosed | vppSTGridPowerMW = if not vpp52STClosed then 0 else vppSTGeneratorPowerMW | immediate model relation | follows 52ST closed feedback | vppSTGridPowerMW | RAW_NODE | IG-036 | PASS | Model source modelica/TripLens_CombinedCycle_TripTAC_ProcessView_v36.mo lines 1136-1137 (cd454995656af9a8747efe8930d2aa0b92f98e1083acadc858eaa7959ea6d2c5); RAW RAW_SESSION_20260924_191347.csv (055f8a21b8f586feafaa6fe6705cfca05b4f1e833713991a0cac1f0e94ad6fd9).; 2026-09-26 PlantControlV2 104046 runtime proof verified 52ST OPEN -> vppSTGridPowerMW = 0 MW. | MODEL_SOURCE_RAW_OBSERVED | Y | SEARCH_ONLY | MODEL_SOURCE_CONFIRMED | USER_RUNTIME_VERIFIED | 282 | 282 | 0 | RUNTIME_VERIFIED
SEQ-52GT-OPEN | GT Protection | 52GT breaker open timing | BREAKER_SEQUENCE | vppGTTripLatch ¦ vppECMS52GTClosedCommandNative | GT latch active -> breaker opens | 0.080 s | - | vpp52GTClosed | RAW_NODE | IG-026 | PASS | vppGTBreakerOpenDelay = 0.080 s; EVENT run observed 48.44 -> 48.520005 | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
SEQ-52GT-TRIPCMD | GT Protection | 52GT trip command timing | BREAKER_SEQUENCE | vppGTTripLatch | GT latch active | 0.055 s | - | vpp52GTTripCmd | RAW_NODE | IG-025 | PASS | vppGTTripCommandDelay = 0.055 s | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
SEQ-52ST-OPEN | ST Protection | 52ST breaker open timing | BREAKER_SEQUENCE | vppSTTripLatchPublished ¦ vppECMS52STClosedCommandNative | ST latch active -> breaker opens | 0.100 s | - | vpp52STClosed | RAW_NODE | IG-028 | PASS | vppSTBreakerOpenDelay = 0.100 s; EVENT run observed 48.44 -> 48.540005 | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME
SEQ-52ST-TRIPCMD | ST Protection | 52ST trip command | BREAKER_SEQUENCE | vppSTTripLatchPublished | ST latch active | 0 s | - | vpp52STTripCmd | RAW_NODE | IG-027 | PASS | Runtime node sequence | LIVE_OPCUA_CENSUS | N | LIVE_RUNTIME

## 02_Input_Groups
input_group_id | input_signature | branch_count | rule_ids | outputs | page_id
IG-001 | vppGTExhaustMassFlowState | 2 | AL-GT-FLOW-L; AL-GT-FLOW-LL | GT.EXHAUST.FLOW.L; GT.EXHAUST.FLOW.LL | IG-001
IG-002 | vppGTExhaustTemperatureK | 2 | AL-GT-TEMP-L; AL-GT-TEMP-LL | GT.EXHAUST.TEMP.L; GT.EXHAUST.TEMP.LL | IG-002
IG-003 | vppHPDrumLevelM | 4 | AL-HP-LEVEL-H; AL-HP-LEVEL-HH; AL-HP-LEVEL-L; AL-HP-LEVEL-LL | HRSG.HP.DRUM.LEVEL.H; HRSG.HP.DRUM.LEVEL.HH; HRSG.HP.DRUM.LEVEL.L; HRSG.HP.DRUM.LEVEL.LL | IG-003
IG-004 | vppHPDrumPressurePa | 2 | AL-HP-PRESS-L; AL-HP-PRESS-LL | HRSG.HP.DRUM.PRESS.L; HRSG.HP.DRUM.PRESS.LL | IG-004
IG-005 | vppHPTurbineSteamFlowTH | 2 | AL-HP-FLOW-L; AL-HP-FLOW-LL | HRSG.HP.STEAM.FLOW.L; HRSG.HP.STEAM.FLOW.LL | IG-005
IG-006 | vppIPDrumLevelM | 4 | AL-IP-LEVEL-H; AL-IP-LEVEL-HH; AL-IP-LEVEL-L; AL-IP-LEVEL-LL | HRSG.IP.DRUM.LEVEL.H; HRSG.IP.DRUM.LEVEL.HH; HRSG.IP.DRUM.LEVEL.L; HRSG.IP.DRUM.LEVEL.LL | IG-006
IG-007 | vppIPDrumPressurePa | 2 | AL-IP-PRESS-L; AL-IP-PRESS-LL | HRSG.IP.DRUM.PRESS.L; HRSG.IP.DRUM.PRESS.LL | IG-007
IG-008 | vppIPTurbineSteamFlowTH | 2 | AL-IP-FLOW-L; AL-IP-FLOW-LL | HRSG.IP.STEAM.FLOW.L; HRSG.IP.STEAM.FLOW.LL | IG-008
IG-009 | vppLPDrumLevelM | 4 | AL-LP-LEVEL-H; AL-LP-LEVEL-HH; AL-LP-LEVEL-L; AL-LP-LEVEL-LL | HRSG.LP.DRUM.LEVEL.H; HRSG.LP.DRUM.LEVEL.HH; HRSG.LP.DRUM.LEVEL.L; HRSG.LP.DRUM.LEVEL.LL | IG-009
IG-010 | vppLPDrumPressurePa | 2 | AL-LP-PRESS-L; AL-LP-PRESS-LL | HRSG.LP.DRUM.PRESS.L; HRSG.LP.DRUM.PRESS.LL | IG-010
IG-011 | vppLPTurbineSteamFlowTH | 2 | AL-LP-FLOW-L; AL-LP-FLOW-LL | HRSG.LP.STEAM.FLOW.L; HRSG.LP.STEAM.FLOW.LL | IG-011
IG-012 | vppExternalTripCommandNative | 1 | PROT-DIRECT-GT | vppCauseDirectGTTrip | IG-012
IG-013 | vppExternalSTTripCommandNative | 1 | PROT-DIRECT-ST | vppCauseDirectSTTrip | IG-013
IG-014 | vppECMS52GTClosedCommandNative ¦ vppGTTripLatchInternal | 1 | PROT-GT-BRK-OPEN | vppCauseGTBreakerOpenWhileRunning | IG-014
IG-015 | vppHPDrumHHRaw | 1 | PROT-HP-DRUM-HH | vppCauseHPDrumHH | IG-015
IG-016 | vppHPDrumLLRaw | 1 | PROT-HP-DRUM-LL | vppCauseHPDrumLL | IG-016
IG-017 | vppIPDrumHHRaw | 1 | PROT-IP-DRUM-HH | vppCauseIPDrumHH | IG-017
IG-018 | vppIPDrumLLRaw | 1 | PROT-IP-DRUM-LL | vppCauseIPDrumLL | IG-018
IG-019 | vppLPDrumHHRaw | 1 | PROT-LP-DRUM-HH | vppCauseLPDrumHH | IG-019
IG-020 | vppLPDrumLLRaw | 1 | PROT-LP-DRUM-LL | vppCauseLPDrumLL | IG-020
IG-021 | vppCauseDirectGTTrip ¦ vppCauseGTBreakerOpenWhileRunning ¦ vppCauseHPDrumLL ¦ vppCauseIPDrumLL ¦ vppCauseLPDrumLL | 1 | PROT-GT-REQUEST | vppGTTripRequest | IG-021
IG-022 | vppCauseDirectSTTrip ¦ vppCauseHPDrumHH ¦ vppCauseIPDrumHH ¦ vppCauseLPDrumHH ¦ vppCauseSTBreakerOpenWhileRunning ¦ vppGTTripRequest | 1 | PROT-ST-REQUEST | vppSTTripRequest | IG-022
IG-023 | vppGTTripRequest ¦ vppGTTripResetNative | 1 | PROT-GT-LATCH | vppGTTripLatch | IG-023
IG-024 | vppSTTripRequest ¦ vppSTTripResetNative | 1 | PROT-ST-LATCH | vppSTTripLatchPublished | IG-024
IG-025 | vppGTTripLatch | 1 | SEQ-52GT-TRIPCMD | vpp52GTTripCmd | IG-025
IG-026 | vppECMS52GTClosedCommandNative ¦ vppGTTripLatch | 1 | SEQ-52GT-OPEN | vpp52GTClosed | IG-026
IG-027 | vppSTTripLatchPublished | 1 | SEQ-52ST-TRIPCMD | vpp52STTripCmd | IG-027
IG-028 | vppECMS52STClosedCommandNative ¦ vppSTTripLatchPublished | 1 | SEQ-52ST-OPEN | vpp52STClosed | IG-028
IG-029 | vpp52GTClosed | 2 | RESP-GT-POWER; RESP-GT-SPEED | vppGTGPowerMW; vppGTGSpeedRPM | IG-029
IG-030 | vppHPFWPTripPushbuttonNative | 1 | CMD-FWP-HP-TRIP | vppHPFWPTripCommandNative; vppHPFWPTripLatchNative; vppVCBA01TripCommandNative | IG-030
IG-031 | vppHPFWPResetPushbuttonNative | 1 | CMD-FWP-HP-RESET | vppHPFWPTripLatchNative | IG-031
IG-032 | vppIPFWPTripPushbuttonNative | 1 | CMD-FWP-IP-TRIP | vppIPFWPTripCommandNative; vppIPFWPTripLatchNative; vppVCBB01TripCommandNative | IG-032
IG-033 | vppIPFWPResetPushbuttonNative | 1 | CMD-FWP-IP-RESET | vppIPFWPTripLatchNative | IG-033
IG-034 | vppLPFWPTripPushbuttonNative | 1 | CMD-FWP-LP-TRIP | vppLPFWPTripCommandNative; vppLPFWPTripLatchNative; vppVCBA02TripCommandNative | IG-034
IG-035 | vppLPFWPResetPushbuttonNative | 1 | CMD-FWP-LP-RESET | vppLPFWPTripLatchNative | IG-035
IG-036 | vpp52STClosed ¦ vppSTGeneratorPowerMW | 1 | RESP-ST-GRID-POWER | vppSTGridPowerMW | IG-036
IG-037 | vppECMS52STClosedCommandNative | 1 | PROT-ST-BRK-OPEN | vppCauseSTBreakerOpenWhileRunning | IG-037

## 03_HP_Drum
rule_id | input_group_id | logic_name | input_nodes | condition | delay | reset_hysteresis | output_nodes_or_tags | validation_status
AL-HP-FLOW-L | IG-005 | HP turbine steam flow L | vppHPTurbineSteamFlowTH | value < 486 t/h | 0.2 s | 10.8 t/h | HRSG.HP.STEAM.FLOW.L | PARTIAL
AL-HP-FLOW-LL | IG-005 | HP turbine steam flow LL | vppHPTurbineSteamFlowTH | value < 324 t/h | 0.2 s | 10.8 t/h | HRSG.HP.STEAM.FLOW.LL | PARTIAL
AL-HP-LEVEL-H | IG-003 | HP drum level H | vppHPDrumLevelM | value > 1.15 m | 0.5 s | 0.02 m | HRSG.HP.DRUM.LEVEL.H | PARTIAL
AL-HP-LEVEL-HH | IG-003 | HP drum level HH | vppHPDrumLevelM | value > 1.25 m | 0.5 s | 0.02 m | HRSG.HP.DRUM.LEVEL.HH | PARTIAL
AL-HP-LEVEL-L | IG-003 | HP drum level L | vppHPDrumLevelM | value < 0.95 m | 0.5 s | 0.02 m | HRSG.HP.DRUM.LEVEL.L | PARTIAL
AL-HP-LEVEL-LL | IG-003 | HP drum level LL | vppHPDrumLevelM | value < 0.85 m | 0.5 s | 0.02 m | HRSG.HP.DRUM.LEVEL.LL | PARTIAL
AL-HP-PRESS-L | IG-004 | HP drum pressure L | vppHPDrumPressurePa | value < 12000000 Pa | 0.5 s | 200000 Pa | HRSG.HP.DRUM.PRESS.L | PARTIAL
AL-HP-PRESS-LL | IG-004 | HP drum pressure LL | vppHPDrumPressurePa | value < 10800000 Pa | 0.5 s | 200000 Pa | HRSG.HP.DRUM.PRESS.LL | PARTIAL
PROT-HP-DRUM-HH | IG-015 | HP drum HH protection cause | vppHPDrumHHRaw | raw HH state == 1 | runtime-defined | reset/return per runtime | vppCauseHPDrumHH | PARTIAL
PROT-HP-DRUM-LL | IG-016 | HP drum LL protection cause | vppHPDrumLLRaw | raw LL state == 1 | runtime-defined | reset/return per runtime | vppCauseHPDrumLL | PARTIAL

## 04_IP_Drum
rule_id | input_group_id | logic_name | input_nodes | condition | delay | reset_hysteresis | output_nodes_or_tags | validation_status
AL-IP-FLOW-L | IG-008 | IP turbine steam flow L | vppIPTurbineSteamFlowTH | value < 576 t/h | 0.2 s | 10.8 t/h | HRSG.IP.STEAM.FLOW.L | PARTIAL
AL-IP-FLOW-LL | IG-008 | IP turbine steam flow LL | vppIPTurbineSteamFlowTH | value < 378 t/h | 0.2 s | 10.8 t/h | HRSG.IP.STEAM.FLOW.LL | PARTIAL
AL-IP-LEVEL-H | IG-006 | IP drum level H | vppIPDrumLevelM | value > 1.15 m | 0.5 s | 0.02 m | HRSG.IP.DRUM.LEVEL.H | PARTIAL
AL-IP-LEVEL-HH | IG-006 | IP drum level HH | vppIPDrumLevelM | value > 1.25 m | 0.5 s | 0.02 m | HRSG.IP.DRUM.LEVEL.HH | PARTIAL
AL-IP-LEVEL-L | IG-006 | IP drum level L | vppIPDrumLevelM | value < 0.95 m | 0.5 s | 0.02 m | HRSG.IP.DRUM.LEVEL.L | PARTIAL
AL-IP-LEVEL-LL | IG-006 | IP drum level LL | vppIPDrumLevelM | value < 0.85 m | 0.5 s | 0.02 m | HRSG.IP.DRUM.LEVEL.LL | PARTIAL
AL-IP-PRESS-L | IG-007 | IP drum pressure L | vppIPDrumPressurePa | value < 2550000 Pa | 0.5 s | 50000 Pa | HRSG.IP.DRUM.PRESS.L | PARTIAL
AL-IP-PRESS-LL | IG-007 | IP drum pressure LL | vppIPDrumPressurePa | value < 2300000 Pa | 0.5 s | 50000 Pa | HRSG.IP.DRUM.PRESS.LL | PARTIAL
PROT-IP-DRUM-HH | IG-017 | IP drum HH protection cause | vppIPDrumHHRaw | raw HH state == 1 | runtime-defined | reset/return per runtime | vppCauseIPDrumHH | PARTIAL
PROT-IP-DRUM-LL | IG-018 | IP drum LL protection cause | vppIPDrumLLRaw | raw LL state == 1 | runtime-defined | reset/return per runtime | vppCauseIPDrumLL | PARTIAL

## 05_LP_Drum
rule_id | input_group_id | logic_name | input_nodes | condition | delay | reset_hysteresis | output_nodes_or_tags | validation_status
AL-LP-FLOW-L | IG-011 | LP turbine steam flow L | vppLPTurbineSteamFlowTH | value < 630 t/h | 0.2 s | 10.8 t/h | HRSG.LP.STEAM.FLOW.L | PARTIAL
AL-LP-FLOW-LL | IG-011 | LP turbine steam flow LL | vppLPTurbineSteamFlowTH | value < 424.8 t/h | 0.2 s | 10.8 t/h | HRSG.LP.STEAM.FLOW.LL | PARTIAL
AL-LP-LEVEL-H | IG-009 | LP drum level H | vppLPDrumLevelM | value > 1.85 m | 0.5 s | 0.02 m | HRSG.LP.DRUM.LEVEL.H | PARTIAL
AL-LP-LEVEL-HH | IG-009 | LP drum level HH | vppLPDrumLevelM | value > 1.95 m | 0.5 s | 0.02 m | HRSG.LP.DRUM.LEVEL.HH | PARTIAL
AL-LP-LEVEL-L | IG-009 | LP drum level L | vppLPDrumLevelM | value < 1.65 m | 0.5 s | 0.02 m | HRSG.LP.DRUM.LEVEL.L | PARTIAL
AL-LP-LEVEL-LL | IG-009 | LP drum level LL | vppLPDrumLevelM | value < 1.55 m | 0.5 s | 0.02 m | HRSG.LP.DRUM.LEVEL.LL | PARTIAL
AL-LP-PRESS-L | IG-010 | LP drum pressure L | vppLPDrumPressurePa | value < 500000 Pa | 0.5 s | 10000 Pa | HRSG.LP.DRUM.PRESS.L | PARTIAL
AL-LP-PRESS-LL | IG-010 | LP drum pressure LL | vppLPDrumPressurePa | value < 450000 Pa | 0.5 s | 10000 Pa | HRSG.LP.DRUM.PRESS.LL | PARTIAL
PROT-LP-DRUM-HH | IG-019 | LP drum HH protection cause | vppLPDrumHHRaw | raw HH state == 1 | runtime-defined | reset/return per runtime | vppCauseLPDrumHH | PARTIAL
PROT-LP-DRUM-LL | IG-020 | LP drum LL protection cause | vppLPDrumLLRaw | raw LL state == 1 | runtime-defined | reset/return per runtime | vppCauseLPDrumLL | PARTIAL

## 06_GT_Exhaust
rule_id | input_group_id | logic_name | input_nodes | condition | delay | reset_hysteresis | output_nodes_or_tags | validation_status
AL-GT-FLOW-L | IG-001 | GT exhaust flow low | vppGTExhaustMassFlowState | value < 545 kg/s | 0.2 s | +6 kg/s | GT.EXHAUST.FLOW.L | PARTIAL
AL-GT-FLOW-LL | IG-001 | GT exhaust flow low-low | vppGTExhaustMassFlowState | value < 300 kg/s | 0.2 s | +6 kg/s | GT.EXHAUST.FLOW.LL | PARTIAL
AL-GT-TEMP-L | IG-002 | GT exhaust temperature low | vppGTExhaustTemperatureK | value < 805 K | 0.2 s | +5 K | GT.EXHAUST.TEMP.L | PARTIAL
AL-GT-TEMP-LL | IG-002 | GT exhaust temperature low-low | vppGTExhaustTemperatureK | value < 580 K | 0.2 s | +5 K | GT.EXHAUST.TEMP.LL | PARTIAL

## 07_GT_Protection
rule_id | input_group_id | logic_name | input_nodes | condition | delay | reset_hysteresis | output_nodes_or_tags | validation_status
PROT-DIRECT-GT | IG-012 | Direct GT trip cause | vppExternalTripCommandNative | command >= 0.5 | 0 s | reset by GT reset | vppCauseDirectGTTrip | PASS
PROT-GT-BRK-OPEN | IG-014 | GT breaker open while running cause | vppECMS52GTClosedCommandNative ¦ vppGTTripLatchInternal | 52GT close command < 0.5 AND GT latch not active | 0 s | state reset | vppCauseGTBreakerOpenWhileRunning | PARTIAL
PROT-GT-LATCH | IG-023 | GT trip latch | vppGTTripRequest ¦ vppGTTripResetNative | request=1 AND reset<0.5 -> latch; reset clears | event-driven | reset input | vppGTTripLatch | PASS
PROT-GT-REQUEST | IG-021 | GT trip request OR matrix | vppCauseDirectGTTrip ¦ vppCauseGTBreakerOpenWhileRunning ¦ vppCauseHPDrumLL ¦ vppCauseIPDrumLL ¦ vppCauseLPDrumLL | OR(all inputs) | 0 s | GT reset | vppGTTripRequest | PASS
RESP-GT-POWER | IG-029 | GT power response after breaker open | vpp52GTClosed | if 52GT not closed then GT generator power = 0 | immediate model relation | - | vppGTGPowerMW | PASS
RESP-GT-SPEED | IG-029 | GT speed coastdown after breaker open | vpp52GTClosed | if 52GT opens, speed decays from nominal by coastdown model | dynamic | - | vppGTGSpeedRPM | PASS
SEQ-52GT-OPEN | IG-026 | 52GT breaker open timing | vppGTTripLatch ¦ vppECMS52GTClosedCommandNative | GT latch active -> breaker opens | 0.080 s | - | vpp52GTClosed | PASS
SEQ-52GT-TRIPCMD | IG-025 | 52GT trip command timing | vppGTTripLatch | GT latch active | 0.055 s | - | vpp52GTTripCmd | PASS

## 08_ST_Protection
rule_id | input_group_id | logic_name | input_nodes | condition | delay | reset_hysteresis | output_nodes_or_tags | validation_status
PROT-DIRECT-ST | IG-013 | Direct ST trip cause | vppExternalSTTripCommandNative | command >= 0.5 | 0 s | reset by ST reset | vppCauseDirectSTTrip | PASS
PROT-ST-LATCH | IG-024 | ST trip latch | vppSTTripRequest ¦ vppSTTripResetNative | request=1 AND reset<0.5 -> latch; reset clears | event-driven | reset input | vppSTTripLatchPublished | PASS
PROT-ST-REQUEST | IG-022 | ST trip request common-trip matrix | vppCauseDirectGTTrip ¦ vppCauseDirectSTTrip ¦ vppCauseGTBreakerOpenWhileRunning ¦ vppCauseHPDrumHH ¦ vppCauseIPDrumHH ¦ vppCauseLPDrumHH ¦ vppCauseHPDrumLL ¦ vppCauseIPDrumLL ¦ vppCauseLPDrumLL | OR(all 9 causes) | 0 s | ST reset | vppSTTripRequest | PASS
SEQ-52ST-OPEN | IG-028 | 52ST breaker open timing | vppSTTripLatchPublished ¦ vppECMS52STClosedCommandNative | ST latch active -> breaker opens | 0.100 s | - | vpp52STClosed | PASS
SEQ-52ST-TRIPCMD | IG-027 | 52ST trip command | vppSTTripLatchPublished | ST latch active | 0 s | - | vpp52STTripCmd | PASS

## 09_FWP_HP
rule_id | input_group_id | logic_name | input_nodes | condition | delay | reset_hysteresis | output_nodes_or_tags | validation_status
CMD-FWP-HP-RESET | IG-031 | HP FWP reset command interface | vppHPFWPResetPushbuttonNative | operator/test reset PB | external runtime interface | - | vppHPFWPTripLatchNative | PARTIAL
CMD-FWP-HP-TRIP | IG-030 | HP FWP trip command interface | vppHPFWPTripPushbuttonNative | operator/test PB writes trip command through runtime interface | external runtime interface | reset PB | vppHPFWPTripCommandNative ¦ vppHPFWPTripLatchNative ¦ vppVCBA01TripCommandNative | PARTIAL

## 10_FWP_IP
rule_id | input_group_id | logic_name | input_nodes | condition | delay | reset_hysteresis | output_nodes_or_tags | validation_status
CMD-FWP-IP-RESET | IG-033 | IP FWP reset command interface | vppIPFWPResetPushbuttonNative | operator/test reset PB | external runtime interface | - | vppIPFWPTripLatchNative | PARTIAL
CMD-FWP-IP-TRIP | IG-032 | IP FWP trip command interface | vppIPFWPTripPushbuttonNative | operator/test PB writes trip command through runtime interface | external runtime interface | reset PB | vppIPFWPTripCommandNative ¦ vppIPFWPTripLatchNative ¦ vppVCBB01TripCommandNative | PARTIAL

## 11_FWP_LP
rule_id | input_group_id | logic_name | input_nodes | condition | delay | reset_hysteresis | output_nodes_or_tags | validation_status
CMD-FWP-LP-RESET | IG-035 | LP FWP reset command interface | vppLPFWPResetPushbuttonNative | operator/test reset PB | external runtime interface | - | vppLPFWPTripLatchNative | PARTIAL
CMD-FWP-LP-TRIP | IG-034 | LP FWP trip command interface | vppLPFWPTripPushbuttonNative | operator/test PB writes trip command through runtime interface | external runtime interface | reset PB | vppLPFWPTripCommandNative ¦ vppLPFWPTripLatchNative ¦ vppVCBA02TripCommandNative | PARTIAL