## 00_ReadMe
metric | value
source_tags | 603
rules | 53
input_groups | 35
equipment_pages | 9
pages | 98
native_inputs | 44
native_outputs | 28
derived_outputs | 28

## 01_Logic_Definition
rule_id | group | logic_name | logic_type | input_nodes | condition | delay | reset_hysteresis | output_nodes_or_tags | output_class | input_group_id | validation_status | source_basis
AL-GT-FLOW-L | GT Exhaust | GT exhaust flow low | ALARM | vppGTExhaustMassFlowState | value < 545 kg/s | 0.2 s | +6 kg/s | GT.EXHAUST.FLOW.L | DERIVED_ALARM | IG-001 | PARTIAL | Current DCS alarm rule; RAW input node exists
AL-GT-FLOW-LL | GT Exhaust | GT exhaust flow low-low | ALARM | vppGTExhaustMassFlowState | value < 300 kg/s | 0.2 s | +6 kg/s | GT.EXHAUST.FLOW.LL | DERIVED_ALARM | IG-001 | PARTIAL | Current DCS alarm rule; RAW input node exists
AL-GT-TEMP-L | GT Exhaust | GT exhaust temperature low | ALARM | vppGTExhaustTemperatureK | value < 805 K | 0.2 s | +5 K | GT.EXHAUST.TEMP.L | DERIVED_ALARM | IG-002 | PARTIAL | Current DCS alarm rule; RAW input node exists
AL-GT-TEMP-LL | GT Exhaust | GT exhaust temperature low-low | ALARM | vppGTExhaustTemperatureK | value < 580 K | 0.2 s | +5 K | GT.EXHAUST.TEMP.LL | DERIVED_ALARM | IG-002 | PARTIAL | Current DCS alarm rule; RAW input node exists
AL-HP-FLOW-L | HP Steam Flow | HP turbine steam flow L | ALARM | vppHPTurbineSteamFlowTH | value < 486 t/h | 0.2 s | 10.8 t/h | HRSG.HP.STEAM.FLOW.L | DERIVED_ALARM | IG-005 | PARTIAL | Current DCS alarm rule; RAW node is vpp*TurbineSteamFlowTH; threshold converted exactly from kg/s × 3.6
AL-HP-FLOW-LL | HP Steam Flow | HP turbine steam flow LL | ALARM | vppHPTurbineSteamFlowTH | value < 324 t/h | 0.2 s | 10.8 t/h | HRSG.HP.STEAM.FLOW.LL | DERIVED_ALARM | IG-005 | PARTIAL | Current DCS alarm rule; RAW node is vpp*TurbineSteamFlowTH; threshold converted exactly from kg/s × 3.6
AL-HP-LEVEL-H | HP Drum | HP drum level H | ALARM | vppHPDrumLevelM | value > 1.15 m | 0.5 s | 0.02 m | HRSG.HP.DRUM.LEVEL.H | DERIVED_ALARM | IG-003 | PARTIAL | Current DCS alarm rule; RAW input node exists
AL-HP-LEVEL-HH | HP Drum | HP drum level HH | ALARM | vppHPDrumLevelM | value > 1.25 m | 0.5 s | 0.02 m | HRSG.HP.DRUM.LEVEL.HH | DERIVED_ALARM | IG-003 | PARTIAL | Current DCS alarm rule; RAW input node exists
AL-HP-LEVEL-L | HP Drum | HP drum level L | ALARM | vppHPDrumLevelM | value < 0.95 m | 0.5 s | 0.02 m | HRSG.HP.DRUM.LEVEL.L | DERIVED_ALARM | IG-003 | PARTIAL | Current DCS alarm rule; RAW input node exists
AL-HP-LEVEL-LL | HP Drum | HP drum level LL | ALARM | vppHPDrumLevelM | value < 0.85 m | 0.5 s | 0.02 m | HRSG.HP.DRUM.LEVEL.LL | DERIVED_ALARM | IG-003 | PARTIAL | Current DCS alarm rule; RAW input node exists
AL-HP-PRESS-L | HP Drum | HP drum pressure L | ALARM | vppHPDrumPressurePa | value < 12000000 Pa | 0.5 s | 200000 Pa | HRSG.HP.DRUM.PRESS.L | DERIVED_ALARM | IG-004 | PARTIAL | Current DCS alarm rule; RAW input node exists
AL-HP-PRESS-LL | HP Drum | HP drum pressure LL | ALARM | vppHPDrumPressurePa | value < 10800000 Pa | 0.5 s | 200000 Pa | HRSG.HP.DRUM.PRESS.LL | DERIVED_ALARM | IG-004 | PARTIAL | Current DCS alarm rule; RAW input node exists
AL-IP-FLOW-L | IP Steam Flow | IP turbine steam flow L | ALARM | vppIPTurbineSteamFlowTH | value < 576 t/h | 0.2 s | 10.8 t/h | HRSG.IP.STEAM.FLOW.L | DERIVED_ALARM | IG-008 | PARTIAL | Current DCS alarm rule; RAW node is vpp*TurbineSteamFlowTH; threshold converted exactly from kg/s × 3.6
AL-IP-FLOW-LL | IP Steam Flow | IP turbine steam flow LL | ALARM | vppIPTurbineSteamFlowTH | value < 378 t/h | 0.2 s | 10.8 t/h | HRSG.IP.STEAM.FLOW.LL | DERIVED_ALARM | IG-008 | PARTIAL | Current DCS alarm rule; RAW node is vpp*TurbineSteamFlowTH; threshold converted exactly from kg/s × 3.6
AL-IP-LEVEL-H | IP Drum | IP drum level H | ALARM | vppIPDrumLevelM | value > 1.15 m | 0.5 s | 0.02 m | HRSG.IP.DRUM.LEVEL.H | DERIVED_ALARM | IG-006 | PARTIAL | Current DCS alarm rule; RAW input node exists
AL-IP-LEVEL-HH | IP Drum | IP drum level HH | ALARM | vppIPDrumLevelM | value > 1.25 m | 0.5 s | 0.02 m | HRSG.IP.DRUM.LEVEL.HH | DERIVED_ALARM | IG-006 | PARTIAL | Current DCS alarm rule; RAW input node exists
AL-IP-LEVEL-L | IP Drum | IP drum level L | ALARM | vppIPDrumLevelM | value < 0.95 m | 0.5 s | 0.02 m | HRSG.IP.DRUM.LEVEL.L | DERIVED_ALARM | IG-006 | PARTIAL | Current DCS alarm rule; RAW input node exists
AL-IP-LEVEL-LL | IP Drum | IP drum level LL | ALARM | vppIPDrumLevelM | value < 0.85 m | 0.5 s | 0.02 m | HRSG.IP.DRUM.LEVEL.LL | DERIVED_ALARM | IG-006 | PARTIAL | Current DCS alarm rule; RAW input node exists
AL-IP-PRESS-L | IP Drum | IP drum pressure L | ALARM | vppIPDrumPressurePa | value < 2550000 Pa | 0.5 s | 50000 Pa | HRSG.IP.DRUM.PRESS.L | DERIVED_ALARM | IG-007 | PARTIAL | Current DCS alarm rule; RAW input node exists
AL-IP-PRESS-LL | IP Drum | IP drum pressure LL | ALARM | vppIPDrumPressurePa | value < 2300000 Pa | 0.5 s | 50000 Pa | HRSG.IP.DRUM.PRESS.LL | DERIVED_ALARM | IG-007 | PARTIAL | Current DCS alarm rule; RAW input node exists
AL-LP-FLOW-L | LP Steam Flow | LP turbine steam flow L | ALARM | vppLPTurbineSteamFlowTH | value < 630 t/h | 0.2 s | 10.8 t/h | HRSG.LP.STEAM.FLOW.L | DERIVED_ALARM | IG-011 | PARTIAL | Current DCS alarm rule; RAW node is vpp*TurbineSteamFlowTH; threshold converted exactly from kg/s × 3.6
AL-LP-FLOW-LL | LP Steam Flow | LP turbine steam flow LL | ALARM | vppLPTurbineSteamFlowTH | value < 424.8 t/h | 0.2 s | 10.8 t/h | HRSG.LP.STEAM.FLOW.LL | DERIVED_ALARM | IG-011 | PARTIAL | Current DCS alarm rule; RAW node is vpp*TurbineSteamFlowTH; threshold converted exactly from kg/s × 3.6
AL-LP-LEVEL-H | LP Drum | LP drum level H | ALARM | vppLPDrumLevelM | value > 1.85 m | 0.5 s | 0.02 m | HRSG.LP.DRUM.LEVEL.H | DERIVED_ALARM | IG-009 | PARTIAL | Current DCS alarm rule; RAW input node exists
AL-LP-LEVEL-HH | LP Drum | LP drum level HH | ALARM | vppLPDrumLevelM | value > 1.95 m | 0.5 s | 0.02 m | HRSG.LP.DRUM.LEVEL.HH | DERIVED_ALARM | IG-009 | PARTIAL | Current DCS alarm rule; RAW input node exists
AL-LP-LEVEL-L | LP Drum | LP drum level L | ALARM | vppLPDrumLevelM | value < 1.65 m | 0.5 s | 0.02 m | HRSG.LP.DRUM.LEVEL.L | DERIVED_ALARM | IG-009 | PARTIAL | Current DCS alarm rule; RAW input node exists
AL-LP-LEVEL-LL | LP Drum | LP drum level LL | ALARM | vppLPDrumLevelM | value < 1.55 m | 0.5 s | 0.02 m | HRSG.LP.DRUM.LEVEL.LL | DERIVED_ALARM | IG-009 | PARTIAL | Current DCS alarm rule; RAW input node exists
AL-LP-PRESS-L | LP Drum | LP drum pressure L | ALARM | vppLPDrumPressurePa | value < 500000 Pa | 0.5 s | 10000 Pa | HRSG.LP.DRUM.PRESS.L | DERIVED_ALARM | IG-010 | PARTIAL | Current DCS alarm rule; RAW input node exists
AL-LP-PRESS-LL | LP Drum | LP drum pressure LL | ALARM | vppLPDrumPressurePa | value < 450000 Pa | 0.5 s | 10000 Pa | HRSG.LP.DRUM.PRESS.LL | DERIVED_ALARM | IG-010 | PARTIAL | Current DCS alarm rule; RAW input node exists
CMD-FWP-HP-RESET | FWP HP | HP FWP reset command interface | COMMAND_INTERFACE | vppHPFWPResetPushbuttonNative | operator/test reset PB | external runtime interface | - | vppHPFWPTripLatchNative | RAW_NODE | IG-031 | PARTIAL | Reset node exists in RAW; exact reset sequencing remains runtime-owned
CMD-FWP-HP-TRIP | FWP HP | HP FWP trip command interface | COMMAND_INTERFACE | vppHPFWPTripPushbuttonNative | operator/test PB writes trip command through runtime interface | external runtime interface | reset PB | vppHPFWPTripCommandNative ¦ vppHPFWPTripLatchNative ¦ vppVCBA01TripCommandNative | RAW_NODE | IG-030 | PARTIAL | All command/latch/breaker nodes exist in RAW; exact client-side sequencing is not re-invented here
CMD-FWP-IP-RESET | FWP IP | IP FWP reset command interface | COMMAND_INTERFACE | vppIPFWPResetPushbuttonNative | operator/test reset PB | external runtime interface | - | vppIPFWPTripLatchNative | RAW_NODE | IG-033 | PARTIAL | Reset node exists in RAW; exact reset sequencing remains runtime-owned
CMD-FWP-IP-TRIP | FWP IP | IP FWP trip command interface | COMMAND_INTERFACE | vppIPFWPTripPushbuttonNative | operator/test PB writes trip command through runtime interface | external runtime interface | reset PB | vppIPFWPTripCommandNative ¦ vppIPFWPTripLatchNative ¦ vppVCBB01TripCommandNative | RAW_NODE | IG-032 | PARTIAL | All command/latch/breaker nodes exist in RAW; exact client-side sequencing is not re-invented here
CMD-FWP-LP-RESET | FWP LP | LP FWP reset command interface | COMMAND_INTERFACE | vppLPFWPResetPushbuttonNative | operator/test reset PB | external runtime interface | - | vppLPFWPTripLatchNative | RAW_NODE | IG-035 | PARTIAL | Reset node exists in RAW; exact reset sequencing remains runtime-owned
CMD-FWP-LP-TRIP | FWP LP | LP FWP trip command interface | COMMAND_INTERFACE | vppLPFWPTripPushbuttonNative | operator/test PB writes trip command through runtime interface | external runtime interface | reset PB | vppLPFWPTripCommandNative ¦ vppLPFWPTripLatchNative ¦ vppVCBA02TripCommandNative | RAW_NODE | IG-034 | PARTIAL | All command/latch/breaker nodes exist in RAW; exact client-side sequencing is not re-invented here
PROT-DIRECT-GT | GT Protection | Direct GT trip cause | PROTECTION_CAUSE | vppExternalTripCommandNative | command >= 0.5 | 0 s | reset by GT reset | vppCauseDirectGTTrip | RAW_NODE | IG-012 | PASS | RAW node + runtime regression evidence
PROT-DIRECT-ST | ST Protection | Direct ST trip cause | PROTECTION_CAUSE | vppExternalSTTripCommandNative | command >= 0.5 | 0 s | reset by ST reset | vppCauseDirectSTTrip | RAW_NODE | IG-013 | PASS | RAW node + runtime regression evidence
PROT-GT-BRK-OPEN | GT Protection | GT breaker open while running cause | PROTECTION_CAUSE | vppECMS52GTClosedCommandNative ¦ vppGTTripLatchInternal | 52GT close command < 0.5 AND GT latch not active | 0 s | state reset | vppCauseGTBreakerOpenWhileRunning | RAW_NODE | IG-014 | PARTIAL | Exact expression recovered from model compile trace
PROT-GT-LATCH | GT Protection | GT trip latch | LATCH | vppGTTripRequest ¦ vppGTTripResetNative | request=1 AND reset<0.5 -> latch; reset clears | event-driven | reset input | vppGTTripLatch | RAW_NODE | IG-023 | PASS | Runtime latch node and request/reset nodes exist
PROT-GT-REQUEST | GT Protection | GT trip request OR matrix | TRIP_REQUEST | vppCauseDirectGTTrip ¦ vppCauseGTBreakerOpenWhileRunning ¦ vppCauseHPDrumLL ¦ vppCauseIPDrumLL ¦ vppCauseLPDrumLL | OR(all inputs) | 0 s | GT reset | vppGTTripRequest | RAW_NODE | IG-021 | PASS | Exact GT request equation recovered from model compile trace
PROT-HP-DRUM-HH | HP Drum Protection | HP drum HH protection cause | PROTECTION_CAUSE | vppHPDrumHHRaw | raw HH state == 1 | runtime-defined | reset/return per runtime | vppCauseHPDrumHH | RAW_NODE | IG-015 | PARTIAL | RAW comparator/cause nodes exist; exact internal debounce retained in runtime
PROT-HP-DRUM-LL | HP Drum Protection | HP drum LL protection cause | PROTECTION_CAUSE | vppHPDrumLLRaw | raw LL state == 1 | runtime-defined | reset/return per runtime | vppCauseHPDrumLL | RAW_NODE | IG-016 | PARTIAL | RAW comparator/cause nodes exist; exact internal debounce retained in runtime
PROT-IP-DRUM-HH | IP Drum Protection | IP drum HH protection cause | PROTECTION_CAUSE | vppIPDrumHHRaw | raw HH state == 1 | runtime-defined | reset/return per runtime | vppCauseIPDrumHH | RAW_NODE | IG-017 | PARTIAL | RAW comparator/cause nodes exist; exact internal debounce retained in runtime
PROT-IP-DRUM-LL | IP Drum Protection | IP drum LL protection cause | PROTECTION_CAUSE | vppIPDrumLLRaw | raw LL state == 1 | runtime-defined | reset/return per runtime | vppCauseIPDrumLL | RAW_NODE | IG-018 | PARTIAL | RAW comparator/cause nodes exist; exact internal debounce retained in runtime
PROT-LP-DRUM-HH | LP Drum Protection | LP drum HH protection cause | PROTECTION_CAUSE | vppLPDrumHHRaw | raw HH state == 1 | runtime-defined | reset/return per runtime | vppCauseLPDrumHH | RAW_NODE | IG-019 | PARTIAL | RAW comparator/cause nodes exist; exact internal debounce retained in runtime
PROT-LP-DRUM-LL | LP Drum Protection | LP drum LL protection cause | PROTECTION_CAUSE | vppLPDrumLLRaw | raw LL state == 1 | runtime-defined | reset/return per runtime | vppCauseLPDrumLL | RAW_NODE | IG-020 | PARTIAL | RAW comparator/cause nodes exist; exact internal debounce retained in runtime
PROT-ST-LATCH | ST Protection | ST trip latch | LATCH | vppSTTripRequest ¦ vppSTTripResetNative | request=1 AND reset<0.5 -> latch; reset clears | event-driven | reset input | vppSTTripLatchPublished | RAW_NODE | IG-024 | PASS | Runtime latch node and request/reset nodes exist
PROT-ST-REQUEST | ST Protection | ST trip request common-trip matrix | TRIP_REQUEST | vppCauseDirectGTTrip ¦ vppCauseDirectSTTrip ¦ vppCauseGTBreakerOpenWhileRunning ¦ vppCauseHPDrumHH ¦ vppCauseIPDrumHH ¦ vppCauseLPDrumHH ¦ vppCauseHPDrumLL ¦ vppCauseIPDrumLL ¦ vppCauseLPDrumLL | OR(all 9 causes) | 0 s | ST reset | vppSTTripRequest | RAW_NODE | IG-022 | PASS | 9-cause common-trip matrix + RAW nodes
RESP-GT-POWER | GT Response | GT power response after breaker open | PHYSICAL_RESPONSE | vpp52GTClosed | if 52GT not closed then GT generator power = 0 | immediate model relation | - | vppGTGPowerMW | RAW_NODE | IG-029 | PASS | Exact model equation
RESP-GT-SPEED | GT Response | GT speed coastdown after breaker open | PHYSICAL_RESPONSE | vpp52GTClosed | if 52GT opens, speed decays from nominal by coastdown model | dynamic | - | vppGTGSpeedRPM | RAW_NODE | IG-029 | PASS | Exact model equation
SEQ-52GT-OPEN | GT Protection | 52GT breaker open timing | BREAKER_SEQUENCE | vppGTTripLatch ¦ vppECMS52GTClosedCommandNative | GT latch active -> breaker opens | 0.080 s | - | vpp52GTClosed | RAW_NODE | IG-026 | PASS | vppGTBreakerOpenDelay = 0.080 s; EVENT run observed 48.44 -> 48.520005
SEQ-52GT-TRIPCMD | GT Protection | 52GT trip command timing | BREAKER_SEQUENCE | vppGTTripLatch | GT latch active | 0.055 s | - | vpp52GTTripCmd | RAW_NODE | IG-025 | PASS | vppGTTripCommandDelay = 0.055 s
SEQ-52ST-OPEN | ST Protection | 52ST breaker open timing | BREAKER_SEQUENCE | vppSTTripLatchPublished ¦ vppECMS52STClosedCommandNative | ST latch active -> breaker opens | 0.100 s | - | vpp52STClosed | RAW_NODE | IG-028 | PASS | vppSTBreakerOpenDelay = 0.100 s; EVENT run observed 48.44 -> 48.540005
SEQ-52ST-TRIPCMD | ST Protection | 52ST trip command | BREAKER_SEQUENCE | vppSTTripLatchPublished | ST latch active | 0 s | - | vpp52STTripCmd | RAW_NODE | IG-027 | PASS | Runtime node sequence

## 02_Ports
rule_id | port_id | relation | node_or_tag | kind
AL-GT-FLOW-L | IN-01 | INPUT | vppGTExhaustMassFlowState | RAW_NODE
AL-GT-FLOW-L | OUT-01 | OUTPUT | GT.EXHAUST.FLOW.L | DERIVED_TAG
AL-GT-FLOW-LL | IN-01 | INPUT | vppGTExhaustMassFlowState | RAW_NODE
AL-GT-FLOW-LL | OUT-01 | OUTPUT | GT.EXHAUST.FLOW.LL | DERIVED_TAG
AL-GT-TEMP-L | IN-01 | INPUT | vppGTExhaustTemperatureK | RAW_NODE
AL-GT-TEMP-L | OUT-01 | OUTPUT | GT.EXHAUST.TEMP.L | DERIVED_TAG
AL-GT-TEMP-LL | IN-01 | INPUT | vppGTExhaustTemperatureK | RAW_NODE
AL-GT-TEMP-LL | OUT-01 | OUTPUT | GT.EXHAUST.TEMP.LL | DERIVED_TAG
AL-HP-FLOW-L | IN-01 | INPUT | vppHPTurbineSteamFlowTH | RAW_NODE
AL-HP-FLOW-L | OUT-01 | OUTPUT | HRSG.HP.STEAM.FLOW.L | DERIVED_TAG
AL-HP-FLOW-LL | IN-01 | INPUT | vppHPTurbineSteamFlowTH | RAW_NODE
AL-HP-FLOW-LL | OUT-01 | OUTPUT | HRSG.HP.STEAM.FLOW.LL | DERIVED_TAG
AL-HP-LEVEL-H | IN-01 | INPUT | vppHPDrumLevelM | RAW_NODE
AL-HP-LEVEL-H | OUT-01 | OUTPUT | HRSG.HP.DRUM.LEVEL.H | DERIVED_TAG
AL-HP-LEVEL-HH | IN-01 | INPUT | vppHPDrumLevelM | RAW_NODE
AL-HP-LEVEL-HH | OUT-01 | OUTPUT | HRSG.HP.DRUM.LEVEL.HH | DERIVED_TAG
AL-HP-LEVEL-L | IN-01 | INPUT | vppHPDrumLevelM | RAW_NODE
AL-HP-LEVEL-L | OUT-01 | OUTPUT | HRSG.HP.DRUM.LEVEL.L | DERIVED_TAG
AL-HP-LEVEL-LL | IN-01 | INPUT | vppHPDrumLevelM | RAW_NODE
AL-HP-LEVEL-LL | OUT-01 | OUTPUT | HRSG.HP.DRUM.LEVEL.LL | DERIVED_TAG
AL-HP-PRESS-L | IN-01 | INPUT | vppHPDrumPressurePa | RAW_NODE
AL-HP-PRESS-L | OUT-01 | OUTPUT | HRSG.HP.DRUM.PRESS.L | DERIVED_TAG
AL-HP-PRESS-LL | IN-01 | INPUT | vppHPDrumPressurePa | RAW_NODE
AL-HP-PRESS-LL | OUT-01 | OUTPUT | HRSG.HP.DRUM.PRESS.LL | DERIVED_TAG
AL-IP-FLOW-L | IN-01 | INPUT | vppIPTurbineSteamFlowTH | RAW_NODE
AL-IP-FLOW-L | OUT-01 | OUTPUT | HRSG.IP.STEAM.FLOW.L | DERIVED_TAG
AL-IP-FLOW-LL | IN-01 | INPUT | vppIPTurbineSteamFlowTH | RAW_NODE
AL-IP-FLOW-LL | OUT-01 | OUTPUT | HRSG.IP.STEAM.FLOW.LL | DERIVED_TAG
AL-IP-LEVEL-H | IN-01 | INPUT | vppIPDrumLevelM | RAW_NODE
AL-IP-LEVEL-H | OUT-01 | OUTPUT | HRSG.IP.DRUM.LEVEL.H | DERIVED_TAG
AL-IP-LEVEL-HH | IN-01 | INPUT | vppIPDrumLevelM | RAW_NODE
AL-IP-LEVEL-HH | OUT-01 | OUTPUT | HRSG.IP.DRUM.LEVEL.HH | DERIVED_TAG
AL-IP-LEVEL-L | IN-01 | INPUT | vppIPDrumLevelM | RAW_NODE
AL-IP-LEVEL-L | OUT-01 | OUTPUT | HRSG.IP.DRUM.LEVEL.L | DERIVED_TAG
AL-IP-LEVEL-LL | IN-01 | INPUT | vppIPDrumLevelM | RAW_NODE
AL-IP-LEVEL-LL | OUT-01 | OUTPUT | HRSG.IP.DRUM.LEVEL.LL | DERIVED_TAG
AL-IP-PRESS-L | IN-01 | INPUT | vppIPDrumPressurePa | RAW_NODE
AL-IP-PRESS-L | OUT-01 | OUTPUT | HRSG.IP.DRUM.PRESS.L | DERIVED_TAG
AL-IP-PRESS-LL | IN-01 | INPUT | vppIPDrumPressurePa | RAW_NODE
AL-IP-PRESS-LL | OUT-01 | OUTPUT | HRSG.IP.DRUM.PRESS.LL | DERIVED_TAG
AL-LP-FLOW-L | IN-01 | INPUT | vppLPTurbineSteamFlowTH | RAW_NODE
AL-LP-FLOW-L | OUT-01 | OUTPUT | HRSG.LP.STEAM.FLOW.L | DERIVED_TAG
AL-LP-FLOW-LL | IN-01 | INPUT | vppLPTurbineSteamFlowTH | RAW_NODE
AL-LP-FLOW-LL | OUT-01 | OUTPUT | HRSG.LP.STEAM.FLOW.LL | DERIVED_TAG
AL-LP-LEVEL-H | IN-01 | INPUT | vppLPDrumLevelM | RAW_NODE
AL-LP-LEVEL-H | OUT-01 | OUTPUT | HRSG.LP.DRUM.LEVEL.H | DERIVED_TAG
AL-LP-LEVEL-HH | IN-01 | INPUT | vppLPDrumLevelM | RAW_NODE
AL-LP-LEVEL-HH | OUT-01 | OUTPUT | HRSG.LP.DRUM.LEVEL.HH | DERIVED_TAG
AL-LP-LEVEL-L | IN-01 | INPUT | vppLPDrumLevelM | RAW_NODE
AL-LP-LEVEL-L | OUT-01 | OUTPUT | HRSG.LP.DRUM.LEVEL.L | DERIVED_TAG
AL-LP-LEVEL-LL | IN-01 | INPUT | vppLPDrumLevelM | RAW_NODE
AL-LP-LEVEL-LL | OUT-01 | OUTPUT | HRSG.LP.DRUM.LEVEL.LL | DERIVED_TAG
AL-LP-PRESS-L | IN-01 | INPUT | vppLPDrumPressurePa | RAW_NODE
AL-LP-PRESS-L | OUT-01 | OUTPUT | HRSG.LP.DRUM.PRESS.L | DERIVED_TAG
AL-LP-PRESS-LL | IN-01 | INPUT | vppLPDrumPressurePa | RAW_NODE
AL-LP-PRESS-LL | OUT-01 | OUTPUT | HRSG.LP.DRUM.PRESS.LL | DERIVED_TAG
CMD-FWP-HP-RESET | IN-01 | INPUT | vppHPFWPResetPushbuttonNative | RAW_NODE
CMD-FWP-HP-RESET | OUT-01 | OUTPUT | vppHPFWPTripLatchNative | RAW_NODE
CMD-FWP-HP-TRIP | IN-01 | INPUT | vppHPFWPTripPushbuttonNative | RAW_NODE
CMD-FWP-HP-TRIP | OUT-01 | OUTPUT | vppHPFWPTripCommandNative | RAW_NODE
CMD-FWP-HP-TRIP | OUT-02 | OUTPUT | vppHPFWPTripLatchNative | RAW_NODE
CMD-FWP-HP-TRIP | OUT-03 | OUTPUT | vppVCBA01TripCommandNative | RAW_NODE
CMD-FWP-IP-RESET | IN-01 | INPUT | vppIPFWPResetPushbuttonNative | RAW_NODE
CMD-FWP-IP-RESET | OUT-01 | OUTPUT | vppIPFWPTripLatchNative | RAW_NODE
CMD-FWP-IP-TRIP | IN-01 | INPUT | vppIPFWPTripPushbuttonNative | RAW_NODE
CMD-FWP-IP-TRIP | OUT-01 | OUTPUT | vppIPFWPTripCommandNative | RAW_NODE
CMD-FWP-IP-TRIP | OUT-02 | OUTPUT | vppIPFWPTripLatchNative | RAW_NODE
CMD-FWP-IP-TRIP | OUT-03 | OUTPUT | vppVCBB01TripCommandNative | RAW_NODE
CMD-FWP-LP-RESET | IN-01 | INPUT | vppLPFWPResetPushbuttonNative | RAW_NODE
CMD-FWP-LP-RESET | OUT-01 | OUTPUT | vppLPFWPTripLatchNative | RAW_NODE
CMD-FWP-LP-TRIP | IN-01 | INPUT | vppLPFWPTripPushbuttonNative | RAW_NODE
CMD-FWP-LP-TRIP | OUT-01 | OUTPUT | vppLPFWPTripCommandNative | RAW_NODE
CMD-FWP-LP-TRIP | OUT-02 | OUTPUT | vppLPFWPTripLatchNative | RAW_NODE
CMD-FWP-LP-TRIP | OUT-03 | OUTPUT | vppVCBA02TripCommandNative | RAW_NODE
PROT-DIRECT-GT | IN-01 | INPUT | vppExternalTripCommandNative | RAW_NODE
PROT-DIRECT-GT | OUT-01 | OUTPUT | vppCauseDirectGTTrip | RAW_NODE
PROT-DIRECT-ST | IN-01 | INPUT | vppExternalSTTripCommandNative | RAW_NODE
PROT-DIRECT-ST | OUT-01 | OUTPUT | vppCauseDirectSTTrip | RAW_NODE
PROT-GT-BRK-OPEN | IN-01 | INPUT | vppECMS52GTClosedCommandNative | RAW_NODE
PROT-GT-BRK-OPEN | IN-02 | INPUT | vppGTTripLatchInternal | RAW_NODE
PROT-GT-BRK-OPEN | OUT-01 | OUTPUT | vppCauseGTBreakerOpenWhileRunning | RAW_NODE
PROT-GT-LATCH | IN-01 | INPUT | vppGTTripRequest | RAW_NODE
PROT-GT-LATCH | IN-02 | INPUT | vppGTTripResetNative | RAW_NODE
PROT-GT-LATCH | OUT-01 | OUTPUT | vppGTTripLatch | RAW_NODE
PROT-GT-REQUEST | IN-01 | INPUT | vppCauseDirectGTTrip | RAW_NODE
PROT-GT-REQUEST | IN-02 | INPUT | vppCauseGTBreakerOpenWhileRunning | RAW_NODE
PROT-GT-REQUEST | IN-03 | INPUT | vppCauseHPDrumLL | RAW_NODE
PROT-GT-REQUEST | IN-04 | INPUT | vppCauseIPDrumLL | RAW_NODE
PROT-GT-REQUEST | IN-05 | INPUT | vppCauseLPDrumLL | RAW_NODE
PROT-GT-REQUEST | OUT-01 | OUTPUT | vppGTTripRequest | RAW_NODE
PROT-HP-DRUM-HH | IN-01 | INPUT | vppHPDrumHHRaw | RAW_NODE
PROT-HP-DRUM-HH | OUT-01 | OUTPUT | vppCauseHPDrumHH | RAW_NODE
PROT-HP-DRUM-LL | IN-01 | INPUT | vppHPDrumLLRaw | RAW_NODE
PROT-HP-DRUM-LL | OUT-01 | OUTPUT | vppCauseHPDrumLL | RAW_NODE
PROT-IP-DRUM-HH | IN-01 | INPUT | vppIPDrumHHRaw | RAW_NODE
PROT-IP-DRUM-HH | OUT-01 | OUTPUT | vppCauseIPDrumHH | RAW_NODE
PROT-IP-DRUM-LL | IN-01 | INPUT | vppIPDrumLLRaw | RAW_NODE
PROT-IP-DRUM-LL | OUT-01 | OUTPUT | vppCauseIPDrumLL | RAW_NODE
PROT-LP-DRUM-HH | IN-01 | INPUT | vppLPDrumHHRaw | RAW_NODE
PROT-LP-DRUM-HH | OUT-01 | OUTPUT | vppCauseLPDrumHH | RAW_NODE
PROT-LP-DRUM-LL | IN-01 | INPUT | vppLPDrumLLRaw | RAW_NODE
PROT-LP-DRUM-LL | OUT-01 | OUTPUT | vppCauseLPDrumLL | RAW_NODE
PROT-ST-LATCH | IN-01 | INPUT | vppSTTripRequest | RAW_NODE
PROT-ST-LATCH | IN-02 | INPUT | vppSTTripResetNative | RAW_NODE
PROT-ST-LATCH | OUT-01 | OUTPUT | vppSTTripLatchPublished | RAW_NODE
PROT-ST-REQUEST | IN-01 | INPUT | vppCauseDirectGTTrip | RAW_NODE
PROT-ST-REQUEST | IN-02 | INPUT | vppCauseDirectSTTrip | RAW_NODE
PROT-ST-REQUEST | IN-03 | INPUT | vppCauseGTBreakerOpenWhileRunning | RAW_NODE
PROT-ST-REQUEST | IN-04 | INPUT | vppCauseHPDrumHH | RAW_NODE
PROT-ST-REQUEST | IN-05 | INPUT | vppCauseIPDrumHH | RAW_NODE
PROT-ST-REQUEST | IN-06 | INPUT | vppCauseLPDrumHH | RAW_NODE
PROT-ST-REQUEST | IN-07 | INPUT | vppCauseHPDrumLL | RAW_NODE
PROT-ST-REQUEST | IN-08 | INPUT | vppCauseIPDrumLL | RAW_NODE
PROT-ST-REQUEST | IN-09 | INPUT | vppCauseLPDrumLL | RAW_NODE
PROT-ST-REQUEST | OUT-01 | OUTPUT | vppSTTripRequest | RAW_NODE
RESP-GT-POWER | IN-01 | INPUT | vpp52GTClosed | RAW_NODE
RESP-GT-POWER | OUT-01 | OUTPUT | vppGTGPowerMW | RAW_NODE
RESP-GT-SPEED | IN-01 | INPUT | vpp52GTClosed | RAW_NODE
RESP-GT-SPEED | OUT-01 | OUTPUT | vppGTGSpeedRPM | RAW_NODE
SEQ-52GT-OPEN | IN-01 | INPUT | vppGTTripLatch | RAW_NODE
SEQ-52GT-OPEN | IN-02 | INPUT | vppECMS52GTClosedCommandNative | RAW_NODE
SEQ-52GT-OPEN | OUT-01 | OUTPUT | vpp52GTClosed | RAW_NODE
SEQ-52GT-TRIPCMD | IN-01 | INPUT | vppGTTripLatch | RAW_NODE
SEQ-52GT-TRIPCMD | OUT-01 | OUTPUT | vpp52GTTripCmd | RAW_NODE
SEQ-52ST-OPEN | IN-01 | INPUT | vppSTTripLatchPublished | RAW_NODE
SEQ-52ST-OPEN | IN-02 | INPUT | vppECMS52STClosedCommandNative | RAW_NODE
SEQ-52ST-OPEN | OUT-01 | OUTPUT | vpp52STClosed | RAW_NODE
SEQ-52ST-TRIPCMD | IN-01 | INPUT | vppSTTripLatchPublished | RAW_NODE
SEQ-52ST-TRIPCMD | OUT-01 | OUTPUT | vpp52STTripCmd | RAW_NODE

## 03_Blocks
rule_id | block_id | block_type | condition_or_label | delay | reset_hysteresis
AL-GT-FLOW-L | logic:AL-GT-FLOW-L | ALARM | value < 545 kg/s | 0.2 s | +6 kg/s
AL-GT-FLOW-L | delay:AL-GT-FLOW-L | TON |  | 0.2 s
AL-GT-FLOW-LL | logic:AL-GT-FLOW-LL | ALARM | value < 300 kg/s | 0.2 s | +6 kg/s
AL-GT-FLOW-LL | delay:AL-GT-FLOW-LL | TON |  | 0.2 s
AL-GT-TEMP-L | logic:AL-GT-TEMP-L | ALARM | value < 805 K | 0.2 s | +5 K
AL-GT-TEMP-L | delay:AL-GT-TEMP-L | TON |  | 0.2 s
AL-GT-TEMP-LL | logic:AL-GT-TEMP-LL | ALARM | value < 580 K | 0.2 s | +5 K
AL-GT-TEMP-LL | delay:AL-GT-TEMP-LL | TON |  | 0.2 s
AL-HP-FLOW-L | logic:AL-HP-FLOW-L | ALARM | value < 486 t/h | 0.2 s | 10.8 t/h
AL-HP-FLOW-L | delay:AL-HP-FLOW-L | TON |  | 0.2 s
AL-HP-FLOW-LL | logic:AL-HP-FLOW-LL | ALARM | value < 324 t/h | 0.2 s | 10.8 t/h
AL-HP-FLOW-LL | delay:AL-HP-FLOW-LL | TON |  | 0.2 s
AL-HP-LEVEL-H | logic:AL-HP-LEVEL-H | ALARM | value > 1.15 m | 0.5 s | 0.02 m
AL-HP-LEVEL-H | delay:AL-HP-LEVEL-H | TON |  | 0.5 s
AL-HP-LEVEL-HH | logic:AL-HP-LEVEL-HH | ALARM | value > 1.25 m | 0.5 s | 0.02 m
AL-HP-LEVEL-HH | delay:AL-HP-LEVEL-HH | TON |  | 0.5 s
AL-HP-LEVEL-L | logic:AL-HP-LEVEL-L | ALARM | value < 0.95 m | 0.5 s | 0.02 m
AL-HP-LEVEL-L | delay:AL-HP-LEVEL-L | TON |  | 0.5 s
AL-HP-LEVEL-LL | logic:AL-HP-LEVEL-LL | ALARM | value < 0.85 m | 0.5 s | 0.02 m
AL-HP-LEVEL-LL | delay:AL-HP-LEVEL-LL | TON |  | 0.5 s
AL-HP-PRESS-L | logic:AL-HP-PRESS-L | ALARM | value < 12000000 Pa | 0.5 s | 200000 Pa
AL-HP-PRESS-L | delay:AL-HP-PRESS-L | TON |  | 0.5 s
AL-HP-PRESS-LL | logic:AL-HP-PRESS-LL | ALARM | value < 10800000 Pa | 0.5 s | 200000 Pa
AL-HP-PRESS-LL | delay:AL-HP-PRESS-LL | TON |  | 0.5 s
AL-IP-FLOW-L | logic:AL-IP-FLOW-L | ALARM | value < 576 t/h | 0.2 s | 10.8 t/h
AL-IP-FLOW-L | delay:AL-IP-FLOW-L | TON |  | 0.2 s
AL-IP-FLOW-LL | logic:AL-IP-FLOW-LL | ALARM | value < 378 t/h | 0.2 s | 10.8 t/h
AL-IP-FLOW-LL | delay:AL-IP-FLOW-LL | TON |  | 0.2 s
AL-IP-LEVEL-H | logic:AL-IP-LEVEL-H | ALARM | value > 1.15 m | 0.5 s | 0.02 m
AL-IP-LEVEL-H | delay:AL-IP-LEVEL-H | TON |  | 0.5 s
AL-IP-LEVEL-HH | logic:AL-IP-LEVEL-HH | ALARM | value > 1.25 m | 0.5 s | 0.02 m
AL-IP-LEVEL-HH | delay:AL-IP-LEVEL-HH | TON |  | 0.5 s
AL-IP-LEVEL-L | logic:AL-IP-LEVEL-L | ALARM | value < 0.95 m | 0.5 s | 0.02 m
AL-IP-LEVEL-L | delay:AL-IP-LEVEL-L | TON |  | 0.5 s
AL-IP-LEVEL-LL | logic:AL-IP-LEVEL-LL | ALARM | value < 0.85 m | 0.5 s | 0.02 m
AL-IP-LEVEL-LL | delay:AL-IP-LEVEL-LL | TON |  | 0.5 s
AL-IP-PRESS-L | logic:AL-IP-PRESS-L | ALARM | value < 2550000 Pa | 0.5 s | 50000 Pa
AL-IP-PRESS-L | delay:AL-IP-PRESS-L | TON |  | 0.5 s
AL-IP-PRESS-LL | logic:AL-IP-PRESS-LL | ALARM | value < 2300000 Pa | 0.5 s | 50000 Pa
AL-IP-PRESS-LL | delay:AL-IP-PRESS-LL | TON |  | 0.5 s
AL-LP-FLOW-L | logic:AL-LP-FLOW-L | ALARM | value < 630 t/h | 0.2 s | 10.8 t/h
AL-LP-FLOW-L | delay:AL-LP-FLOW-L | TON |  | 0.2 s
AL-LP-FLOW-LL | logic:AL-LP-FLOW-LL | ALARM | value < 424.8 t/h | 0.2 s | 10.8 t/h
AL-LP-FLOW-LL | delay:AL-LP-FLOW-LL | TON |  | 0.2 s
AL-LP-LEVEL-H | logic:AL-LP-LEVEL-H | ALARM | value > 1.85 m | 0.5 s | 0.02 m
AL-LP-LEVEL-H | delay:AL-LP-LEVEL-H | TON |  | 0.5 s
AL-LP-LEVEL-HH | logic:AL-LP-LEVEL-HH | ALARM | value > 1.95 m | 0.5 s | 0.02 m
AL-LP-LEVEL-HH | delay:AL-LP-LEVEL-HH | TON |  | 0.5 s
AL-LP-LEVEL-L | logic:AL-LP-LEVEL-L | ALARM | value < 1.65 m | 0.5 s | 0.02 m
AL-LP-LEVEL-L | delay:AL-LP-LEVEL-L | TON |  | 0.5 s
AL-LP-LEVEL-LL | logic:AL-LP-LEVEL-LL | ALARM | value < 1.55 m | 0.5 s | 0.02 m
AL-LP-LEVEL-LL | delay:AL-LP-LEVEL-LL | TON |  | 0.5 s
AL-LP-PRESS-L | logic:AL-LP-PRESS-L | ALARM | value < 500000 Pa | 0.5 s | 10000 Pa
AL-LP-PRESS-L | delay:AL-LP-PRESS-L | TON |  | 0.5 s
AL-LP-PRESS-LL | logic:AL-LP-PRESS-LL | ALARM | value < 450000 Pa | 0.5 s | 10000 Pa
AL-LP-PRESS-LL | delay:AL-LP-PRESS-LL | TON |  | 0.5 s
CMD-FWP-HP-RESET | logic:CMD-FWP-HP-RESET | COMMAND_INTERFACE | operator/test reset PB | external runtime interface | -
CMD-FWP-HP-TRIP | logic:CMD-FWP-HP-TRIP | COMMAND_INTERFACE | operator/test PB writes trip command through runtime interface | external runtime interface | reset PB
CMD-FWP-IP-RESET | logic:CMD-FWP-IP-RESET | COMMAND_INTERFACE | operator/test reset PB | external runtime interface | -
CMD-FWP-IP-TRIP | logic:CMD-FWP-IP-TRIP | COMMAND_INTERFACE | operator/test PB writes trip command through runtime interface | external runtime interface | reset PB
CMD-FWP-LP-RESET | logic:CMD-FWP-LP-RESET | COMMAND_INTERFACE | operator/test reset PB | external runtime interface | -
CMD-FWP-LP-TRIP | logic:CMD-FWP-LP-TRIP | COMMAND_INTERFACE | operator/test PB writes trip command through runtime interface | external runtime interface | reset PB
PROT-DIRECT-GT | logic:PROT-DIRECT-GT | PROTECTION_CAUSE | command >= 0.5 | 0 s | reset by GT reset
PROT-DIRECT-ST | logic:PROT-DIRECT-ST | PROTECTION_CAUSE | command >= 0.5 | 0 s | reset by ST reset
PROT-GT-BRK-OPEN | logic:PROT-GT-BRK-OPEN | PROTECTION_CAUSE | 52GT close command < 0.5 AND GT latch not active | 0 s | state reset
PROT-GT-LATCH | logic:PROT-GT-LATCH | LATCH | request=1 AND reset<0.5 -> latch; reset clears | event-driven | reset input
PROT-GT-REQUEST | logic:PROT-GT-REQUEST | TRIP_REQUEST | OR(all inputs) | 0 s | GT reset
PROT-HP-DRUM-HH | logic:PROT-HP-DRUM-HH | PROTECTION_CAUSE | raw HH state == 1 | runtime-defined | reset/return per runtime
PROT-HP-DRUM-LL | logic:PROT-HP-DRUM-LL | PROTECTION_CAUSE | raw LL state == 1 | runtime-defined | reset/return per runtime
PROT-IP-DRUM-HH | logic:PROT-IP-DRUM-HH | PROTECTION_CAUSE | raw HH state == 1 | runtime-defined | reset/return per runtime
PROT-IP-DRUM-LL | logic:PROT-IP-DRUM-LL | PROTECTION_CAUSE | raw LL state == 1 | runtime-defined | reset/return per runtime
PROT-LP-DRUM-HH | logic:PROT-LP-DRUM-HH | PROTECTION_CAUSE | raw HH state == 1 | runtime-defined | reset/return per runtime
PROT-LP-DRUM-LL | logic:PROT-LP-DRUM-LL | PROTECTION_CAUSE | raw LL state == 1 | runtime-defined | reset/return per runtime
PROT-ST-LATCH | logic:PROT-ST-LATCH | LATCH | request=1 AND reset<0.5 -> latch; reset clears | event-driven | reset input
PROT-ST-REQUEST | logic:PROT-ST-REQUEST | TRIP_REQUEST | OR(all 9 causes) | 0 s | ST reset
RESP-GT-POWER | logic:RESP-GT-POWER | PHYSICAL_RESPONSE | if 52GT not closed then GT generator power = 0 | immediate model relation | -
RESP-GT-SPEED | logic:RESP-GT-SPEED | PHYSICAL_RESPONSE | if 52GT opens, speed decays from nominal by coastdown model | dynamic | -
SEQ-52GT-OPEN | logic:SEQ-52GT-OPEN | BREAKER_SEQUENCE | GT latch active -> breaker opens | 0.080 s | -
SEQ-52GT-OPEN | delay:SEQ-52GT-OPEN | DEFINED_DELAY |  | 0.080 s
SEQ-52GT-TRIPCMD | logic:SEQ-52GT-TRIPCMD | BREAKER_SEQUENCE | GT latch active | 0.055 s | -
SEQ-52GT-TRIPCMD | delay:SEQ-52GT-TRIPCMD | DEFINED_DELAY |  | 0.055 s
SEQ-52ST-OPEN | logic:SEQ-52ST-OPEN | BREAKER_SEQUENCE | ST latch active -> breaker opens | 0.100 s | -
SEQ-52ST-OPEN | delay:SEQ-52ST-OPEN | DEFINED_DELAY |  | 0.100 s
SEQ-52ST-TRIPCMD | logic:SEQ-52ST-TRIPCMD | BREAKER_SEQUENCE | ST latch active | 0 s | -

## 04_Edges
rule_id | from_id | to_id | edge_role
AL-GT-FLOW-L | logic:AL-GT-FLOW-L | delay:AL-GT-FLOW-L | DEFINED_DELAY
AL-GT-FLOW-L | PORT:IN-01 | logic:AL-GT-FLOW-L | INPUT
AL-GT-FLOW-L | delay:AL-GT-FLOW-L | PORT:OUT-01 | OUTPUT
AL-GT-FLOW-LL | logic:AL-GT-FLOW-LL | delay:AL-GT-FLOW-LL | DEFINED_DELAY
AL-GT-FLOW-LL | PORT:IN-01 | logic:AL-GT-FLOW-LL | INPUT
AL-GT-FLOW-LL | delay:AL-GT-FLOW-LL | PORT:OUT-01 | OUTPUT
AL-GT-TEMP-L | logic:AL-GT-TEMP-L | delay:AL-GT-TEMP-L | DEFINED_DELAY
AL-GT-TEMP-L | PORT:IN-01 | logic:AL-GT-TEMP-L | INPUT
AL-GT-TEMP-L | delay:AL-GT-TEMP-L | PORT:OUT-01 | OUTPUT
AL-GT-TEMP-LL | logic:AL-GT-TEMP-LL | delay:AL-GT-TEMP-LL | DEFINED_DELAY
AL-GT-TEMP-LL | PORT:IN-01 | logic:AL-GT-TEMP-LL | INPUT
AL-GT-TEMP-LL | delay:AL-GT-TEMP-LL | PORT:OUT-01 | OUTPUT
AL-HP-FLOW-L | logic:AL-HP-FLOW-L | delay:AL-HP-FLOW-L | DEFINED_DELAY
AL-HP-FLOW-L | PORT:IN-01 | logic:AL-HP-FLOW-L | INPUT
AL-HP-FLOW-L | delay:AL-HP-FLOW-L | PORT:OUT-01 | OUTPUT
AL-HP-FLOW-LL | logic:AL-HP-FLOW-LL | delay:AL-HP-FLOW-LL | DEFINED_DELAY
AL-HP-FLOW-LL | PORT:IN-01 | logic:AL-HP-FLOW-LL | INPUT
AL-HP-FLOW-LL | delay:AL-HP-FLOW-LL | PORT:OUT-01 | OUTPUT
AL-HP-LEVEL-H | logic:AL-HP-LEVEL-H | delay:AL-HP-LEVEL-H | DEFINED_DELAY
AL-HP-LEVEL-H | PORT:IN-01 | logic:AL-HP-LEVEL-H | INPUT
AL-HP-LEVEL-H | delay:AL-HP-LEVEL-H | PORT:OUT-01 | OUTPUT
AL-HP-LEVEL-HH | logic:AL-HP-LEVEL-HH | delay:AL-HP-LEVEL-HH | DEFINED_DELAY
AL-HP-LEVEL-HH | PORT:IN-01 | logic:AL-HP-LEVEL-HH | INPUT
AL-HP-LEVEL-HH | delay:AL-HP-LEVEL-HH | PORT:OUT-01 | OUTPUT
AL-HP-LEVEL-L | logic:AL-HP-LEVEL-L | delay:AL-HP-LEVEL-L | DEFINED_DELAY
AL-HP-LEVEL-L | PORT:IN-01 | logic:AL-HP-LEVEL-L | INPUT
AL-HP-LEVEL-L | delay:AL-HP-LEVEL-L | PORT:OUT-01 | OUTPUT
AL-HP-LEVEL-LL | logic:AL-HP-LEVEL-LL | delay:AL-HP-LEVEL-LL | DEFINED_DELAY
AL-HP-LEVEL-LL | PORT:IN-01 | logic:AL-HP-LEVEL-LL | INPUT
AL-HP-LEVEL-LL | delay:AL-HP-LEVEL-LL | PORT:OUT-01 | OUTPUT
AL-HP-PRESS-L | logic:AL-HP-PRESS-L | delay:AL-HP-PRESS-L | DEFINED_DELAY
AL-HP-PRESS-L | PORT:IN-01 | logic:AL-HP-PRESS-L | INPUT
AL-HP-PRESS-L | delay:AL-HP-PRESS-L | PORT:OUT-01 | OUTPUT
AL-HP-PRESS-LL | logic:AL-HP-PRESS-LL | delay:AL-HP-PRESS-LL | DEFINED_DELAY
AL-HP-PRESS-LL | PORT:IN-01 | logic:AL-HP-PRESS-LL | INPUT
AL-HP-PRESS-LL | delay:AL-HP-PRESS-LL | PORT:OUT-01 | OUTPUT
AL-IP-FLOW-L | logic:AL-IP-FLOW-L | delay:AL-IP-FLOW-L | DEFINED_DELAY
AL-IP-FLOW-L | PORT:IN-01 | logic:AL-IP-FLOW-L | INPUT
AL-IP-FLOW-L | delay:AL-IP-FLOW-L | PORT:OUT-01 | OUTPUT
AL-IP-FLOW-LL | logic:AL-IP-FLOW-LL | delay:AL-IP-FLOW-LL | DEFINED_DELAY
AL-IP-FLOW-LL | PORT:IN-01 | logic:AL-IP-FLOW-LL | INPUT
AL-IP-FLOW-LL | delay:AL-IP-FLOW-LL | PORT:OUT-01 | OUTPUT
AL-IP-LEVEL-H | logic:AL-IP-LEVEL-H | delay:AL-IP-LEVEL-H | DEFINED_DELAY
AL-IP-LEVEL-H | PORT:IN-01 | logic:AL-IP-LEVEL-H | INPUT
AL-IP-LEVEL-H | delay:AL-IP-LEVEL-H | PORT:OUT-01 | OUTPUT
AL-IP-LEVEL-HH | logic:AL-IP-LEVEL-HH | delay:AL-IP-LEVEL-HH | DEFINED_DELAY
AL-IP-LEVEL-HH | PORT:IN-01 | logic:AL-IP-LEVEL-HH | INPUT
AL-IP-LEVEL-HH | delay:AL-IP-LEVEL-HH | PORT:OUT-01 | OUTPUT
AL-IP-LEVEL-L | logic:AL-IP-LEVEL-L | delay:AL-IP-LEVEL-L | DEFINED_DELAY
AL-IP-LEVEL-L | PORT:IN-01 | logic:AL-IP-LEVEL-L | INPUT
AL-IP-LEVEL-L | delay:AL-IP-LEVEL-L | PORT:OUT-01 | OUTPUT
AL-IP-LEVEL-LL | logic:AL-IP-LEVEL-LL | delay:AL-IP-LEVEL-LL | DEFINED_DELAY
AL-IP-LEVEL-LL | PORT:IN-01 | logic:AL-IP-LEVEL-LL | INPUT
AL-IP-LEVEL-LL | delay:AL-IP-LEVEL-LL | PORT:OUT-01 | OUTPUT
AL-IP-PRESS-L | logic:AL-IP-PRESS-L | delay:AL-IP-PRESS-L | DEFINED_DELAY
AL-IP-PRESS-L | PORT:IN-01 | logic:AL-IP-PRESS-L | INPUT
AL-IP-PRESS-L | delay:AL-IP-PRESS-L | PORT:OUT-01 | OUTPUT
AL-IP-PRESS-LL | logic:AL-IP-PRESS-LL | delay:AL-IP-PRESS-LL | DEFINED_DELAY
AL-IP-PRESS-LL | PORT:IN-01 | logic:AL-IP-PRESS-LL | INPUT
AL-IP-PRESS-LL | delay:AL-IP-PRESS-LL | PORT:OUT-01 | OUTPUT
AL-LP-FLOW-L | logic:AL-LP-FLOW-L | delay:AL-LP-FLOW-L | DEFINED_DELAY
AL-LP-FLOW-L | PORT:IN-01 | logic:AL-LP-FLOW-L | INPUT
AL-LP-FLOW-L | delay:AL-LP-FLOW-L | PORT:OUT-01 | OUTPUT
AL-LP-FLOW-LL | logic:AL-LP-FLOW-LL | delay:AL-LP-FLOW-LL | DEFINED_DELAY
AL-LP-FLOW-LL | PORT:IN-01 | logic:AL-LP-FLOW-LL | INPUT
AL-LP-FLOW-LL | delay:AL-LP-FLOW-LL | PORT:OUT-01 | OUTPUT
AL-LP-LEVEL-H | logic:AL-LP-LEVEL-H | delay:AL-LP-LEVEL-H | DEFINED_DELAY
AL-LP-LEVEL-H | PORT:IN-01 | logic:AL-LP-LEVEL-H | INPUT
AL-LP-LEVEL-H | delay:AL-LP-LEVEL-H | PORT:OUT-01 | OUTPUT
AL-LP-LEVEL-HH | logic:AL-LP-LEVEL-HH | delay:AL-LP-LEVEL-HH | DEFINED_DELAY
AL-LP-LEVEL-HH | PORT:IN-01 | logic:AL-LP-LEVEL-HH | INPUT
AL-LP-LEVEL-HH | delay:AL-LP-LEVEL-HH | PORT:OUT-01 | OUTPUT
AL-LP-LEVEL-L | logic:AL-LP-LEVEL-L | delay:AL-LP-LEVEL-L | DEFINED_DELAY
AL-LP-LEVEL-L | PORT:IN-01 | logic:AL-LP-LEVEL-L | INPUT
AL-LP-LEVEL-L | delay:AL-LP-LEVEL-L | PORT:OUT-01 | OUTPUT
AL-LP-LEVEL-LL | logic:AL-LP-LEVEL-LL | delay:AL-LP-LEVEL-LL | DEFINED_DELAY
AL-LP-LEVEL-LL | PORT:IN-01 | logic:AL-LP-LEVEL-LL | INPUT
AL-LP-LEVEL-LL | delay:AL-LP-LEVEL-LL | PORT:OUT-01 | OUTPUT
AL-LP-PRESS-L | logic:AL-LP-PRESS-L | delay:AL-LP-PRESS-L | DEFINED_DELAY
AL-LP-PRESS-L | PORT:IN-01 | logic:AL-LP-PRESS-L | INPUT
AL-LP-PRESS-L | delay:AL-LP-PRESS-L | PORT:OUT-01 | OUTPUT
AL-LP-PRESS-LL | logic:AL-LP-PRESS-LL | delay:AL-LP-PRESS-LL | DEFINED_DELAY
AL-LP-PRESS-LL | PORT:IN-01 | logic:AL-LP-PRESS-LL | INPUT
AL-LP-PRESS-LL | delay:AL-LP-PRESS-LL | PORT:OUT-01 | OUTPUT
CMD-FWP-HP-RESET | PORT:IN-01 | logic:CMD-FWP-HP-RESET | INPUT
CMD-FWP-HP-RESET | logic:CMD-FWP-HP-RESET | PORT:OUT-01 | OUTPUT
CMD-FWP-HP-TRIP | PORT:IN-01 | logic:CMD-FWP-HP-TRIP | INPUT
CMD-FWP-HP-TRIP | logic:CMD-FWP-HP-TRIP | PORT:OUT-01 | OUTPUT
CMD-FWP-HP-TRIP | logic:CMD-FWP-HP-TRIP | PORT:OUT-02 | OUTPUT
CMD-FWP-HP-TRIP | logic:CMD-FWP-HP-TRIP | PORT:OUT-03 | OUTPUT
CMD-FWP-IP-RESET | PORT:IN-01 | logic:CMD-FWP-IP-RESET | INPUT
CMD-FWP-IP-RESET | logic:CMD-FWP-IP-RESET | PORT:OUT-01 | OUTPUT
CMD-FWP-IP-TRIP | PORT:IN-01 | logic:CMD-FWP-IP-TRIP | INPUT
CMD-FWP-IP-TRIP | logic:CMD-FWP-IP-TRIP | PORT:OUT-01 | OUTPUT
CMD-FWP-IP-TRIP | logic:CMD-FWP-IP-TRIP | PORT:OUT-02 | OUTPUT
CMD-FWP-IP-TRIP | logic:CMD-FWP-IP-TRIP | PORT:OUT-03 | OUTPUT
CMD-FWP-LP-RESET | PORT:IN-01 | logic:CMD-FWP-LP-RESET | INPUT
CMD-FWP-LP-RESET | logic:CMD-FWP-LP-RESET | PORT:OUT-01 | OUTPUT
CMD-FWP-LP-TRIP | PORT:IN-01 | logic:CMD-FWP-LP-TRIP | INPUT
CMD-FWP-LP-TRIP | logic:CMD-FWP-LP-TRIP | PORT:OUT-01 | OUTPUT
CMD-FWP-LP-TRIP | logic:CMD-FWP-LP-TRIP | PORT:OUT-02 | OUTPUT
CMD-FWP-LP-TRIP | logic:CMD-FWP-LP-TRIP | PORT:OUT-03 | OUTPUT
PROT-DIRECT-GT | PORT:IN-01 | logic:PROT-DIRECT-GT | INPUT
PROT-DIRECT-GT | logic:PROT-DIRECT-GT | PORT:OUT-01 | OUTPUT
PROT-DIRECT-ST | PORT:IN-01 | logic:PROT-DIRECT-ST | INPUT
PROT-DIRECT-ST | logic:PROT-DIRECT-ST | PORT:OUT-01 | OUTPUT
PROT-GT-BRK-OPEN | PORT:IN-01 | logic:PROT-GT-BRK-OPEN | INPUT
PROT-GT-BRK-OPEN | PORT:IN-02 | logic:PROT-GT-BRK-OPEN | INPUT
PROT-GT-BRK-OPEN | logic:PROT-GT-BRK-OPEN | PORT:OUT-01 | OUTPUT
PROT-GT-LATCH | PORT:IN-01 | logic:PROT-GT-LATCH | INPUT
PROT-GT-LATCH | PORT:IN-02 | logic:PROT-GT-LATCH | INPUT
PROT-GT-LATCH | logic:PROT-GT-LATCH | PORT:OUT-01 | OUTPUT
PROT-GT-REQUEST | PORT:IN-01 | logic:PROT-GT-REQUEST | INPUT
PROT-GT-REQUEST | PORT:IN-02 | logic:PROT-GT-REQUEST | INPUT
PROT-GT-REQUEST | PORT:IN-03 | logic:PROT-GT-REQUEST | INPUT
PROT-GT-REQUEST | PORT:IN-04 | logic:PROT-GT-REQUEST | INPUT
PROT-GT-REQUEST | PORT:IN-05 | logic:PROT-GT-REQUEST | INPUT
PROT-GT-REQUEST | logic:PROT-GT-REQUEST | PORT:OUT-01 | OUTPUT
PROT-HP-DRUM-HH | PORT:IN-01 | logic:PROT-HP-DRUM-HH | INPUT
PROT-HP-DRUM-HH | logic:PROT-HP-DRUM-HH | PORT:OUT-01 | OUTPUT
PROT-HP-DRUM-LL | PORT:IN-01 | logic:PROT-HP-DRUM-LL | INPUT
PROT-HP-DRUM-LL | logic:PROT-HP-DRUM-LL | PORT:OUT-01 | OUTPUT
PROT-IP-DRUM-HH | PORT:IN-01 | logic:PROT-IP-DRUM-HH | INPUT
PROT-IP-DRUM-HH | logic:PROT-IP-DRUM-HH | PORT:OUT-01 | OUTPUT
PROT-IP-DRUM-LL | PORT:IN-01 | logic:PROT-IP-DRUM-LL | INPUT
PROT-IP-DRUM-LL | logic:PROT-IP-DRUM-LL | PORT:OUT-01 | OUTPUT
PROT-LP-DRUM-HH | PORT:IN-01 | logic:PROT-LP-DRUM-HH | INPUT
PROT-LP-DRUM-HH | logic:PROT-LP-DRUM-HH | PORT:OUT-01 | OUTPUT
PROT-LP-DRUM-LL | PORT:IN-01 | logic:PROT-LP-DRUM-LL | INPUT
PROT-LP-DRUM-LL | logic:PROT-LP-DRUM-LL | PORT:OUT-01 | OUTPUT
PROT-ST-LATCH | PORT:IN-01 | logic:PROT-ST-LATCH | INPUT
PROT-ST-LATCH | PORT:IN-02 | logic:PROT-ST-LATCH | INPUT
PROT-ST-LATCH | logic:PROT-ST-LATCH | PORT:OUT-01 | OUTPUT
PROT-ST-REQUEST | PORT:IN-01 | logic:PROT-ST-REQUEST | INPUT
PROT-ST-REQUEST | PORT:IN-02 | logic:PROT-ST-REQUEST | INPUT
PROT-ST-REQUEST | PORT:IN-03 | logic:PROT-ST-REQUEST | INPUT
PROT-ST-REQUEST | PORT:IN-04 | logic:PROT-ST-REQUEST | INPUT
PROT-ST-REQUEST | PORT:IN-05 | logic:PROT-ST-REQUEST | INPUT
PROT-ST-REQUEST | PORT:IN-06 | logic:PROT-ST-REQUEST | INPUT
PROT-ST-REQUEST | PORT:IN-07 | logic:PROT-ST-REQUEST | INPUT
PROT-ST-REQUEST | PORT:IN-08 | logic:PROT-ST-REQUEST | INPUT
PROT-ST-REQUEST | PORT:IN-09 | logic:PROT-ST-REQUEST | INPUT
PROT-ST-REQUEST | logic:PROT-ST-REQUEST | PORT:OUT-01 | OUTPUT
RESP-GT-POWER | PORT:IN-01 | logic:RESP-GT-POWER | INPUT
RESP-GT-POWER | logic:RESP-GT-POWER | PORT:OUT-01 | OUTPUT
RESP-GT-SPEED | PORT:IN-01 | logic:RESP-GT-SPEED | INPUT
RESP-GT-SPEED | logic:RESP-GT-SPEED | PORT:OUT-01 | OUTPUT
SEQ-52GT-OPEN | logic:SEQ-52GT-OPEN | delay:SEQ-52GT-OPEN | DEFINED_DELAY
SEQ-52GT-OPEN | PORT:IN-01 | logic:SEQ-52GT-OPEN | INPUT
SEQ-52GT-OPEN | PORT:IN-02 | logic:SEQ-52GT-OPEN | INPUT
SEQ-52GT-OPEN | delay:SEQ-52GT-OPEN | PORT:OUT-01 | OUTPUT
SEQ-52GT-TRIPCMD | logic:SEQ-52GT-TRIPCMD | delay:SEQ-52GT-TRIPCMD | DEFINED_DELAY
SEQ-52GT-TRIPCMD | PORT:IN-01 | logic:SEQ-52GT-TRIPCMD | INPUT
SEQ-52GT-TRIPCMD | delay:SEQ-52GT-TRIPCMD | PORT:OUT-01 | OUTPUT
SEQ-52ST-OPEN | logic:SEQ-52ST-OPEN | delay:SEQ-52ST-OPEN | DEFINED_DELAY
SEQ-52ST-OPEN | PORT:IN-01 | logic:SEQ-52ST-OPEN | INPUT
SEQ-52ST-OPEN | PORT:IN-02 | logic:SEQ-52ST-OPEN | INPUT
SEQ-52ST-OPEN | delay:SEQ-52ST-OPEN | PORT:OUT-01 | OUTPUT
SEQ-52ST-TRIPCMD | PORT:IN-01 | logic:SEQ-52ST-TRIPCMD | INPUT
SEQ-52ST-TRIPCMD | logic:SEQ-52ST-TRIPCMD | PORT:OUT-01 | OUTPUT