## 00_Verification
TripLens Logic Master — 53 Run 54 live rules + separate source-mapped rule / Current V8
Check | Result | Expected | Status
Current logic rows | 53 | 53 | PASS
Unique source input nodes live | 44 | 44 | PASS
Rules with all inputs live | 53 | 53 | PASS
Unique vpp source/model outputs live | 28 | 28 | PASS
Local derived alarm outputs | 28 | 28 | SEPARATED
Missing live input nodes | 0 | 0 | PASS
Missing live vpp output nodes | 0 | 0 | PASS
Scenario Lab-only inventory command logic | 0 | 0 | PASS
Live Tag Master source nodes | 603 | 603 | PASS
Validation evidence | Actions #54 / 35309650110 | https://github.com/khaku25/triplens-thermosyspro-cloud-runner/actions/runs/35309650110 | TRACE
Behavior evidence | Run #41 columns retained separately | Identity/current-existence is determined by Run #54 live census | INFO
Source-mapped model rules | 1 | 1 | MODEL_SOURCE_CONFIRMED
RAW behavior scope | 282 closed / 0 open | closed-only observation | PARTIAL
52ST OPEN test | NOT_TESTED | no open-breaker RAW rows | NOT_TESTED

## 01_Logic_Master_Current
rule_id | group | logic_name | logic_type | input_nodes | condition | delay | reset_hysteresis | output_nodes_or_tags | output_class | raw_inputs_exist | raw_outputs_exist | validation_status | source_basis | notes | input_group_id | input_signature | branch_count | branch_index | run41_status | release_status | run41_evidence_scenarios | run41_evidence_note | input_identity_status | output_identity_status | hallucination_audit_status | live_input_status | live_output_status | live_validation_run | live_validation_note
AL-GT-FLOW-L | GT Exhaust | GT exhaust flow low | ALARM | vppGTExhaustMassFlowState | value < 545 kg/s | 0.2 s | +6 kg/s | GT.EXHAUST.FLOW.L | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW input node exists |  | IG-001 | vppGTExhaustMassFlowState | 2 | 1 | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-GT-FLOW-LL | GT Exhaust | GT exhaust flow low-low | ALARM | vppGTExhaustMassFlowState | value < 300 kg/s | 0.2 s | +6 kg/s | GT.EXHAUST.FLOW.LL | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW input node exists |  | IG-001 | vppGTExhaustMassFlowState | 2 | 2 | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-GT-TEMP-L | GT Exhaust | GT exhaust temperature low | ALARM | vppGTExhaustTemperatureK | value < 805 K | 0.2 s | +5 K | GT.EXHAUST.TEMP.L | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW input node exists |  | IG-002 | vppGTExhaustTemperatureK | 2 | 1 | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-GT-TEMP-LL | GT Exhaust | GT exhaust temperature low-low | ALARM | vppGTExhaustTemperatureK | value < 580 K | 0.2 s | +5 K | GT.EXHAUST.TEMP.LL | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW input node exists |  | IG-002 | vppGTExhaustTemperatureK | 2 | 2 | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-HP-LEVEL-H | HP Drum | HP drum level H | ALARM | vppHPDrumLevelM | value > 1.15 m | 0.5 s | 0.02 m | HRSG.HP.DRUM.LEVEL.H | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW input node exists |  | IG-003 | vppHPDrumLevelM | 4 | 1 | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-HP-LEVEL-HH | HP Drum | HP drum level HH | ALARM | vppHPDrumLevelM | value > 1.25 m | 0.5 s | 0.02 m | HRSG.HP.DRUM.LEVEL.HH | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW input node exists |  | IG-003 | vppHPDrumLevelM | 4 | 2 | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-HP-LEVEL-L | HP Drum | HP drum level L | ALARM | vppHPDrumLevelM | value < 0.95 m | 0.5 s | 0.02 m | HRSG.HP.DRUM.LEVEL.L | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW input node exists |  | IG-003 | vppHPDrumLevelM | 4 | 3 | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-HP-LEVEL-LL | HP Drum | HP drum level LL | ALARM | vppHPDrumLevelM | value < 0.85 m | 0.5 s | 0.02 m | HRSG.HP.DRUM.LEVEL.LL | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW input node exists |  | IG-003 | vppHPDrumLevelM | 4 | 4 | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-HP-PRESS-L | HP Drum | HP drum pressure L | ALARM | vppHPDrumPressurePa | value < 12000000 Pa | 0.5 s | 200000 Pa | HRSG.HP.DRUM.PRESS.L | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW input node exists |  | IG-004 | vppHPDrumPressurePa | 2 | 1 | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-HP-PRESS-LL | HP Drum | HP drum pressure LL | ALARM | vppHPDrumPressurePa | value < 10800000 Pa | 0.5 s | 200000 Pa | HRSG.HP.DRUM.PRESS.LL | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW input node exists |  | IG-004 | vppHPDrumPressurePa | 2 | 2 | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-HP-FLOW-L | HP Steam Flow | HP turbine steam flow L | ALARM | vppHPTurbineSteamFlowTH | value < 486 t/h | 0.2 s | 10.8 t/h | HRSG.HP.STEAM.FLOW.L | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW node is vpp*TurbineSteamFlowTH; threshold converted exactly from kg/s × 3.6 |  | IG-005 | vppHPTurbineSteamFlowTH | 2 | 1 | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-HP-FLOW-LL | HP Steam Flow | HP turbine steam flow LL | ALARM | vppHPTurbineSteamFlowTH | value < 324 t/h | 0.2 s | 10.8 t/h | HRSG.HP.STEAM.FLOW.LL | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW node is vpp*TurbineSteamFlowTH; threshold converted exactly from kg/s × 3.6 |  | IG-005 | vppHPTurbineSteamFlowTH | 2 | 2 | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-IP-LEVEL-H | IP Drum | IP drum level H | ALARM | vppIPDrumLevelM | value > 1.15 m | 0.5 s | 0.02 m | HRSG.IP.DRUM.LEVEL.H | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW input node exists |  | IG-006 | vppIPDrumLevelM | 4 | 1 | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-IP-LEVEL-HH | IP Drum | IP drum level HH | ALARM | vppIPDrumLevelM | value > 1.25 m | 0.5 s | 0.02 m | HRSG.IP.DRUM.LEVEL.HH | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW input node exists |  | IG-006 | vppIPDrumLevelM | 4 | 2 | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-IP-LEVEL-L | IP Drum | IP drum level L | ALARM | vppIPDrumLevelM | value < 0.95 m | 0.5 s | 0.02 m | HRSG.IP.DRUM.LEVEL.L | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW input node exists |  | IG-006 | vppIPDrumLevelM | 4 | 3 | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-IP-LEVEL-LL | IP Drum | IP drum level LL | ALARM | vppIPDrumLevelM | value < 0.85 m | 0.5 s | 0.02 m | HRSG.IP.DRUM.LEVEL.LL | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW input node exists |  | IG-006 | vppIPDrumLevelM | 4 | 4 | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-IP-PRESS-L | IP Drum | IP drum pressure L | ALARM | vppIPDrumPressurePa | value < 2550000 Pa | 0.5 s | 50000 Pa | HRSG.IP.DRUM.PRESS.L | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW input node exists |  | IG-007 | vppIPDrumPressurePa | 2 | 1 | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-IP-PRESS-LL | IP Drum | IP drum pressure LL | ALARM | vppIPDrumPressurePa | value < 2300000 Pa | 0.5 s | 50000 Pa | HRSG.IP.DRUM.PRESS.LL | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW input node exists |  | IG-007 | vppIPDrumPressurePa | 2 | 2 | RUN41_BOUND_NOT_TRIGGERED | RC_BOUND_ONLY |  | Rule/source bound in Run #41, but no ACTIVE event was observed. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-IP-FLOW-L | IP Steam Flow | IP turbine steam flow L | ALARM | vppIPTurbineSteamFlowTH | value < 576 t/h | 0.2 s | 10.8 t/h | HRSG.IP.STEAM.FLOW.L | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW node is vpp*TurbineSteamFlowTH; threshold converted exactly from kg/s × 3.6 |  | IG-008 | vppIPTurbineSteamFlowTH | 2 | 1 | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-IP-FLOW-LL | IP Steam Flow | IP turbine steam flow LL | ALARM | vppIPTurbineSteamFlowTH | value < 378 t/h | 0.2 s | 10.8 t/h | HRSG.IP.STEAM.FLOW.LL | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW node is vpp*TurbineSteamFlowTH; threshold converted exactly from kg/s × 3.6 |  | IG-008 | vppIPTurbineSteamFlowTH | 2 | 2 | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-LP-LEVEL-H | LP Drum | LP drum level H | ALARM | vppLPDrumLevelM | value > 1.85 m | 0.5 s | 0.02 m | HRSG.LP.DRUM.LEVEL.H | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW input node exists |  | IG-009 | vppLPDrumLevelM | 4 | 1 | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-LP-LEVEL-HH | LP Drum | LP drum level HH | ALARM | vppLPDrumLevelM | value > 1.95 m | 0.5 s | 0.02 m | HRSG.LP.DRUM.LEVEL.HH | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW input node exists |  | IG-009 | vppLPDrumLevelM | 4 | 2 | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-LP-LEVEL-L | LP Drum | LP drum level L | ALARM | vppLPDrumLevelM | value < 1.65 m | 0.5 s | 0.02 m | HRSG.LP.DRUM.LEVEL.L | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW input node exists |  | IG-009 | vppLPDrumLevelM | 4 | 3 | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-LP-LEVEL-LL | LP Drum | LP drum level LL | ALARM | vppLPDrumLevelM | value < 1.55 m | 0.5 s | 0.02 m | HRSG.LP.DRUM.LEVEL.LL | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW input node exists |  | IG-009 | vppLPDrumLevelM | 4 | 4 | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-LP-PRESS-L | LP Drum | LP drum pressure L | ALARM | vppLPDrumPressurePa | value < 500000 Pa | 0.5 s | 10000 Pa | HRSG.LP.DRUM.PRESS.L | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW input node exists |  | IG-010 | vppLPDrumPressurePa | 2 | 1 | RUN41_BOUND_NOT_TRIGGERED | RC_BOUND_ONLY |  | Rule/source bound in Run #41, but no ACTIVE event was observed. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-LP-PRESS-LL | LP Drum | LP drum pressure LL | ALARM | vppLPDrumPressurePa | value < 450000 Pa | 0.5 s | 10000 Pa | HRSG.LP.DRUM.PRESS.LL | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW input node exists |  | IG-010 | vppLPDrumPressurePa | 2 | 2 | RUN41_BOUND_NOT_TRIGGERED | RC_BOUND_ONLY |  | Rule/source bound in Run #41, but no ACTIVE event was observed. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-LP-FLOW-L | LP Steam Flow | LP turbine steam flow L | ALARM | vppLPTurbineSteamFlowTH | value < 630 t/h | 0.2 s | 10.8 t/h | HRSG.LP.STEAM.FLOW.L | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW node is vpp*TurbineSteamFlowTH; threshold converted exactly from kg/s × 3.6 |  | IG-011 | vppLPTurbineSteamFlowTH | 2 | 1 | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
AL-LP-FLOW-LL | LP Steam Flow | LP turbine steam flow LL | ALARM | vppLPTurbineSteamFlowTH | value < 424.8 t/h | 0.2 s | 10.8 t/h | HRSG.LP.STEAM.FLOW.LL | DERIVED_ALARM | Y | Y | PARTIAL | Current DCS alarm rule; RAW node is vpp*TurbineSteamFlowTH; threshold converted exactly from kg/s × 3.6 |  | IG-011 | vppLPTurbineSteamFlowTH | 2 | 2 | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=0 live=0; local_derived_outputs=1
PROT-DIRECT-GT | GT Protection | Direct GT trip cause | PROTECTION_CAUSE | vppExternalTripCommandNative | command >= 0.5 | 0 s | reset by GT reset | vppCauseDirectGTTrip | RAW_NODE | Y | Y | PASS | RAW node + runtime regression evidence |  | IG-012 | vppExternalTripCommandNative | 1 | 1 | RUN41_PROVEN_ASSERTED | RC_CONFIRMED | direct_gt | Protection cause asserted in a passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=1 live=1; local_derived_outputs=0
PROT-DIRECT-ST | ST Protection | Direct ST trip cause | PROTECTION_CAUSE | vppExternalSTTripCommandNative | command >= 0.5 | 0 s | reset by ST reset | vppCauseDirectSTTrip | RAW_NODE | Y | Y | PASS | RAW node + runtime regression evidence |  | IG-013 | vppExternalSTTripCommandNative | 1 | 1 | RUN41_PROVEN_ASSERTED | RC_CONFIRMED | direct_st | Protection cause asserted in a passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=1 live=1; local_derived_outputs=0
PROT-GT-BRK-OPEN | GT Protection | GT breaker open while running cause | PROTECTION_CAUSE | vppECMS52GTClosedCommandNative ¦ vppGTTripLatchInternal | 52GT close command < 0.5 AND GT latch not active | 0 s | state reset | vppCauseGTBreakerOpenWhileRunning | RAW_NODE | Y | Y | PARTIAL | Exact expression recovered from model compile trace |  | IG-014 | vppECMS52GTClosedCommandNative ¦ vppGTTripLatchInternal | 1 | 1 | RUN41_PROVEN_ASSERTED | RC_CONFIRMED | gt_breaker | Protection cause asserted in a passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | inputs=2 live=2; vpp_outputs=1 live=1; local_derived_outputs=0
PROT-HP-DRUM-HH | HP Drum Protection | HP drum HH protection cause | PROTECTION_CAUSE | vppHPDrumHHRaw | raw HH state == 1 | runtime-defined | reset/return per runtime | vppCauseHPDrumHH | RAW_NODE | Y | Y | PARTIAL | RAW comparator/cause nodes exist; exact internal debounce retained in runtime |  | IG-015 | vppHPDrumHHRaw | 1 | 1 | RUN41_PROVEN_ASSERTED | RC_CONFIRMED | hp_drum_hh | Protection cause asserted in a passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=1 live=1; local_derived_outputs=0
PROT-HP-DRUM-LL | HP Drum Protection | HP drum LL protection cause | PROTECTION_CAUSE | vppHPDrumLLRaw | raw LL state == 1 | runtime-defined | reset/return per runtime | vppCauseHPDrumLL | RAW_NODE | Y | Y | PARTIAL | RAW comparator/cause nodes exist; exact internal debounce retained in runtime |  | IG-016 | vppHPDrumLLRaw | 1 | 1 | RUN41_PROVEN_ASSERTED | RC_CONFIRMED | hp_drum_ll | Protection cause asserted in a passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=1 live=1; local_derived_outputs=0
PROT-IP-DRUM-HH | IP Drum Protection | IP drum HH protection cause | PROTECTION_CAUSE | vppIPDrumHHRaw | raw HH state == 1 | runtime-defined | reset/return per runtime | vppCauseIPDrumHH | RAW_NODE | Y | Y | PARTIAL | RAW comparator/cause nodes exist; exact internal debounce retained in runtime |  | IG-017 | vppIPDrumHHRaw | 1 | 1 | RUN41_PROVEN_ASSERTED | RC_CONFIRMED | ip_drum_hh | Protection cause asserted in a passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=1 live=1; local_derived_outputs=0
PROT-IP-DRUM-LL | IP Drum Protection | IP drum LL protection cause | PROTECTION_CAUSE | vppIPDrumLLRaw | raw LL state == 1 | runtime-defined | reset/return per runtime | vppCauseIPDrumLL | RAW_NODE | Y | Y | PARTIAL | RAW comparator/cause nodes exist; exact internal debounce retained in runtime |  | IG-018 | vppIPDrumLLRaw | 1 | 1 | RUN41_PROVEN_ASSERTED | RC_CONFIRMED | ip_drum_ll | Protection cause asserted in a passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=1 live=1; local_derived_outputs=0
PROT-LP-DRUM-HH | LP Drum Protection | LP drum HH protection cause | PROTECTION_CAUSE | vppLPDrumHHRaw | raw HH state == 1 | runtime-defined | reset/return per runtime | vppCauseLPDrumHH | RAW_NODE | Y | Y | PARTIAL | RAW comparator/cause nodes exist; exact internal debounce retained in runtime |  | IG-019 | vppLPDrumHHRaw | 1 | 1 | RUN41_PROVEN_ASSERTED | RC_CONFIRMED | lp_drum_hh | Protection cause asserted in a passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=1 live=1; local_derived_outputs=0
PROT-LP-DRUM-LL | LP Drum Protection | LP drum LL protection cause | PROTECTION_CAUSE | vppLPDrumLLRaw | raw LL state == 1 | runtime-defined | reset/return per runtime | vppCauseLPDrumLL | RAW_NODE | Y | Y | PARTIAL | RAW comparator/cause nodes exist; exact internal debounce retained in runtime |  | IG-020 | vppLPDrumLLRaw | 1 | 1 | RUN41_PROVEN_ASSERTED | RC_CONFIRMED | lp_drum_ll | Protection cause asserted in a passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=1 live=1; local_derived_outputs=0
PROT-GT-REQUEST | GT Protection | GT trip request OR matrix | TRIP_REQUEST | vppCauseDirectGTTrip ¦ vppCauseGTBreakerOpenWhileRunning ¦ vppCauseHPDrumLL ¦ vppCauseIPDrumLL ¦ vppCauseLPDrumLL | OR(all inputs) | 0 s | GT reset | vppGTTripRequest | RAW_NODE | Y | Y | PASS | Exact GT request equation recovered from model compile trace |  | IG-021 | vppCauseDirectGTTrip ¦ vppCauseGTBreakerOpenWhileRunning ¦ vppCauseHPDrumLL ¦ vppCauseIPDrumLL ¦ vppCauseLPDrumLL | 1 | 1 | RUN41_PROVEN | RC_CONFIRMED | direct_gt | Observed in Run #41 direct_gt RAW/EVENT chain. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | inputs=5 live=5; vpp_outputs=1 live=1; local_derived_outputs=0
PROT-ST-REQUEST | ST Protection | ST trip request common-trip matrix | TRIP_REQUEST | vppCauseDirectGTTrip ¦ vppCauseDirectSTTrip ¦ vppCauseGTBreakerOpenWhileRunning ¦ vppCauseHPDrumHH ¦ vppCauseIPDrumHH ¦ vppCauseLPDrumHH ¦ vppCauseHPDrumLL ¦ vppCauseIPDrumLL ¦ vppCauseLPDrumLL | OR(all 9 causes) | 0 s | ST reset | vppSTTripRequest | RAW_NODE | Y | Y | PASS | 9-cause common-trip matrix + RAW nodes |  | IG-022 | vppCauseDirectGTTrip ¦ vppCauseDirectSTTrip ¦ vppCauseGTBreakerOpenWhileRunning ¦ vppCauseHPDrumHH ¦ vppCauseHPDrumLL ¦ vppCauseIPDrumHH ¦ vppCauseIPDrumLL ¦ vppCauseLPDrumHH ¦ vppCauseLPDrumLL | 1 | 1 | RUN41_PROVEN | RC_CONFIRMED | direct_gt | Observed in Run #41 direct_gt RAW/EVENT chain. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | inputs=9 live=9; vpp_outputs=1 live=1; local_derived_outputs=0
PROT-GT-LATCH | GT Protection | GT trip latch | LATCH | vppGTTripRequest ¦ vppGTTripResetNative | request=1 AND reset<0.5 -> latch; reset clears | event-driven | reset input | vppGTTripLatch | RAW_NODE | Y | Y | PASS | Runtime latch node and request/reset nodes exist |  | IG-023 | vppGTTripRequest ¦ vppGTTripResetNative | 1 | 1 | RUN41_PROVEN | RC_CONFIRMED | direct_gt | Observed in Run #41 direct_gt RAW/EVENT chain. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | inputs=2 live=2; vpp_outputs=1 live=1; local_derived_outputs=0
PROT-ST-LATCH | ST Protection | ST trip latch | LATCH | vppSTTripRequest ¦ vppSTTripResetNative | request=1 AND reset<0.5 -> latch; reset clears | event-driven | reset input | vppSTTripLatchPublished | RAW_NODE | Y | Y | PASS | Runtime latch node and request/reset nodes exist |  | IG-024 | vppSTTripRequest ¦ vppSTTripResetNative | 1 | 1 | RUN41_PROVEN | RC_CONFIRMED | direct_gt | Observed in Run #41 direct_gt RAW/EVENT chain. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | inputs=2 live=2; vpp_outputs=1 live=1; local_derived_outputs=0
SEQ-52GT-TRIPCMD | GT Protection | 52GT trip command timing | BREAKER_SEQUENCE | vppGTTripLatch | GT latch active | 0.055 s | - | vpp52GTTripCmd | RAW_NODE | Y | Y | PASS | vppGTTripCommandDelay = 0.055 s |  | IG-025 | vppGTTripLatch | 1 | 1 | RUN41_PROVEN | RC_CONFIRMED | direct_gt | Observed in Run #41 direct_gt RAW/EVENT chain. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=1 live=1; local_derived_outputs=0
SEQ-52GT-OPEN | GT Protection | 52GT breaker open timing | BREAKER_SEQUENCE | vppGTTripLatch ¦ vppECMS52GTClosedCommandNative | GT latch active -> breaker opens | 0.080 s | - | vpp52GTClosed | RAW_NODE | Y | Y | PASS | vppGTBreakerOpenDelay = 0.080 s; EVENT run observed 48.44 -> 48.520005 |  | IG-026 | vppECMS52GTClosedCommandNative ¦ vppGTTripLatch | 1 | 1 | RUN41_PROVEN | RC_CONFIRMED | direct_gt | Observed in Run #41 direct_gt RAW/EVENT chain. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | inputs=2 live=2; vpp_outputs=1 live=1; local_derived_outputs=0
SEQ-52ST-TRIPCMD | ST Protection | 52ST trip command | BREAKER_SEQUENCE | vppSTTripLatchPublished | ST latch active | 0 s | - | vpp52STTripCmd | RAW_NODE | Y | Y | PASS | Runtime node sequence |  | IG-027 | vppSTTripLatchPublished | 1 | 1 | RUN41_PROVEN | RC_CONFIRMED | direct_gt | Observed in Run #41 direct_gt RAW/EVENT chain. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=1 live=1; local_derived_outputs=0
SEQ-52ST-OPEN | ST Protection | 52ST breaker open timing | BREAKER_SEQUENCE | vppSTTripLatchPublished ¦ vppECMS52STClosedCommandNative | ST latch active -> breaker opens | 0.100 s | - | vpp52STClosed | RAW_NODE | Y | Y | PASS | vppSTBreakerOpenDelay = 0.100 s; EVENT run observed 48.44 -> 48.540005 |  | IG-028 | vppECMS52STClosedCommandNative ¦ vppSTTripLatchPublished | 1 | 1 | RUN41_PROVEN | RC_CONFIRMED | direct_gt | Observed in Run #41 direct_gt RAW/EVENT chain. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | inputs=2 live=2; vpp_outputs=1 live=1; local_derived_outputs=0
RESP-GT-POWER | GT Response | GT power response after breaker open | PHYSICAL_RESPONSE | vpp52GTClosed | if 52GT not closed then GT generator power = 0 | immediate model relation | - | vppGTGPowerMW | RAW_NODE | Y | Y | PASS | Exact model equation |  | IG-029 | vpp52GTClosed | 2 | 1 | RUN41_PROVEN | RC_CONFIRMED | direct_gt | Observed in Run #41 direct_gt RAW/EVENT chain. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=1 live=1; local_derived_outputs=0
RESP-GT-SPEED | GT Response | GT speed coastdown after breaker open | PHYSICAL_RESPONSE | vpp52GTClosed | if 52GT opens, speed decays from nominal by coastdown model | dynamic | - | vppGTGSpeedRPM | RAW_NODE | Y | Y | PASS | Exact model equation |  | IG-029 | vpp52GTClosed | 2 | 2 | RUN41_PROVEN | RC_CONFIRMED | direct_gt | Observed in Run #41 direct_gt RAW/EVENT chain. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=1 live=1; local_derived_outputs=0
CMD-FWP-HP-TRIP | FWP HP | HP FWP trip command interface | COMMAND_INTERFACE | vppHPFWPTripPushbuttonNative | operator/test PB writes trip command through runtime interface | external runtime interface | reset PB | vppHPFWPTripCommandNative ¦ vppHPFWPTripLatchNative ¦ vppVCBA01TripCommandNative | RAW_NODE | Y | Y | PARTIAL | All command/latch/breaker nodes exist in RAW; exact client-side sequencing is not re-invented here |  | IG-030 | vppHPFWPTripPushbuttonNative | 1 | 1 | RUN41_FAILED_NOT_PROVEN | RC_NOT_CONFIRMED | hp_bfp | Run #41 hp_bfp did not prove latch/breaker/physical trip chain before model stall. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=3 live=3; local_derived_outputs=0
CMD-FWP-HP-RESET | FWP HP | HP FWP reset command interface | COMMAND_INTERFACE | vppHPFWPResetPushbuttonNative | operator/test reset PB | external runtime interface | - | vppHPFWPTripLatchNative | RAW_NODE | Y | Y | PARTIAL | Reset node exists in RAW; exact reset sequencing remains runtime-owned |  | IG-031 | vppHPFWPResetPushbuttonNative | 1 | 1 | NOT_RUN41 | SOURCE_DEFINED_NOT_RUN41 |  | Reset path exists in source but was not exercised in Run #41. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=1 live=1; local_derived_outputs=0
CMD-FWP-IP-TRIP | FWP IP | IP FWP trip command interface | COMMAND_INTERFACE | vppIPFWPTripPushbuttonNative | operator/test PB writes trip command through runtime interface | external runtime interface | reset PB | vppIPFWPTripCommandNative ¦ vppIPFWPTripLatchNative ¦ vppVCBB01TripCommandNative | RAW_NODE | Y | Y | PARTIAL | All command/latch/breaker nodes exist in RAW; exact client-side sequencing is not re-invented here |  | IG-032 | vppIPFWPTripPushbuttonNative | 1 | 1 | RUN41_PROVEN | RC_CONFIRMED | ip_bfp | Run #41 ip_bfp passed. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=3 live=3; local_derived_outputs=0
CMD-FWP-IP-RESET | FWP IP | IP FWP reset command interface | COMMAND_INTERFACE | vppIPFWPResetPushbuttonNative | operator/test reset PB | external runtime interface | - | vppIPFWPTripLatchNative | RAW_NODE | Y | Y | PARTIAL | Reset node exists in RAW; exact reset sequencing remains runtime-owned |  | IG-033 | vppIPFWPResetPushbuttonNative | 1 | 1 | NOT_RUN41 | SOURCE_DEFINED_NOT_RUN41 |  | Reset path exists in source but was not exercised in Run #41. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=1 live=1; local_derived_outputs=0
CMD-FWP-LP-TRIP | FWP LP | LP FWP trip command interface | COMMAND_INTERFACE | vppLPFWPTripPushbuttonNative | operator/test PB writes trip command through runtime interface | external runtime interface | reset PB | vppLPFWPTripCommandNative ¦ vppLPFWPTripLatchNative ¦ vppVCBA02TripCommandNative | RAW_NODE | Y | Y | PARTIAL | All command/latch/breaker nodes exist in RAW; exact client-side sequencing is not re-invented here |  | IG-034 | vppLPFWPTripPushbuttonNative | 1 | 1 | RUN41_PARTIAL_ELECTRICAL | RC_PARTIAL | lp_bfp | LP electrical trip chain changed, but NRV/drum/common-trip downstream path was not proven before stall. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=3 live=3; local_derived_outputs=0
CMD-FWP-LP-RESET | FWP LP | LP FWP reset command interface | COMMAND_INTERFACE | vppLPFWPResetPushbuttonNative | operator/test reset PB | external runtime interface | - | vppLPFWPTripLatchNative | RAW_NODE | Y | Y | PARTIAL | Reset node exists in RAW; exact reset sequencing remains runtime-owned |  | IG-035 | vppLPFWPResetPushbuttonNative | 1 | 1 | NOT_RUN41 | SOURCE_DEFINED_NOT_RUN41 |  | Reset path exists in source but was not exercised in Run #41. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | inputs=1 live=1; vpp_outputs=1 live=1; local_derived_outputs=0

## 02_Logic_Edges
rule_id | group | edge_role | from_node | to_node | label | timing
AL-GT-FLOW-L | GT Exhaust | INPUT | vppGTExhaustMassFlowState | LOGIC | value < 545 kg/s | 0.2 s
AL-GT-FLOW-L | GT Exhaust | OUTPUT | LOGIC | GT.EXHAUST.FLOW.L | DERIVED_ALARM
AL-GT-FLOW-LL | GT Exhaust | INPUT | vppGTExhaustMassFlowState | LOGIC | value < 300 kg/s | 0.2 s
AL-GT-FLOW-LL | GT Exhaust | OUTPUT | LOGIC | GT.EXHAUST.FLOW.LL | DERIVED_ALARM
AL-GT-TEMP-L | GT Exhaust | INPUT | vppGTExhaustTemperatureK | LOGIC | value < 805 K | 0.2 s
AL-GT-TEMP-L | GT Exhaust | OUTPUT | LOGIC | GT.EXHAUST.TEMP.L | DERIVED_ALARM
AL-GT-TEMP-LL | GT Exhaust | INPUT | vppGTExhaustTemperatureK | LOGIC | value < 580 K | 0.2 s
AL-GT-TEMP-LL | GT Exhaust | OUTPUT | LOGIC | GT.EXHAUST.TEMP.LL | DERIVED_ALARM
AL-HP-LEVEL-H | HP Drum | INPUT | vppHPDrumLevelM | LOGIC | value > 1.15 m | 0.5 s
AL-HP-LEVEL-H | HP Drum | OUTPUT | LOGIC | HRSG.HP.DRUM.LEVEL.H | DERIVED_ALARM
AL-HP-LEVEL-HH | HP Drum | INPUT | vppHPDrumLevelM | LOGIC | value > 1.25 m | 0.5 s
AL-HP-LEVEL-HH | HP Drum | OUTPUT | LOGIC | HRSG.HP.DRUM.LEVEL.HH | DERIVED_ALARM
AL-HP-LEVEL-L | HP Drum | INPUT | vppHPDrumLevelM | LOGIC | value < 0.95 m | 0.5 s
AL-HP-LEVEL-L | HP Drum | OUTPUT | LOGIC | HRSG.HP.DRUM.LEVEL.L | DERIVED_ALARM
AL-HP-LEVEL-LL | HP Drum | INPUT | vppHPDrumLevelM | LOGIC | value < 0.85 m | 0.5 s
AL-HP-LEVEL-LL | HP Drum | OUTPUT | LOGIC | HRSG.HP.DRUM.LEVEL.LL | DERIVED_ALARM
AL-HP-PRESS-L | HP Drum | INPUT | vppHPDrumPressurePa | LOGIC | value < 12000000 Pa | 0.5 s
AL-HP-PRESS-L | HP Drum | OUTPUT | LOGIC | HRSG.HP.DRUM.PRESS.L | DERIVED_ALARM
AL-HP-PRESS-LL | HP Drum | INPUT | vppHPDrumPressurePa | LOGIC | value < 10800000 Pa | 0.5 s
AL-HP-PRESS-LL | HP Drum | OUTPUT | LOGIC | HRSG.HP.DRUM.PRESS.LL | DERIVED_ALARM
AL-HP-FLOW-L | HP Steam Flow | INPUT | vppHPTurbineSteamFlowTH | LOGIC | value < 486 t/h | 0.2 s
AL-HP-FLOW-L | HP Steam Flow | OUTPUT | LOGIC | HRSG.HP.STEAM.FLOW.L | DERIVED_ALARM
AL-HP-FLOW-LL | HP Steam Flow | INPUT | vppHPTurbineSteamFlowTH | LOGIC | value < 324 t/h | 0.2 s
AL-HP-FLOW-LL | HP Steam Flow | OUTPUT | LOGIC | HRSG.HP.STEAM.FLOW.LL | DERIVED_ALARM
AL-IP-LEVEL-H | IP Drum | INPUT | vppIPDrumLevelM | LOGIC | value > 1.15 m | 0.5 s
AL-IP-LEVEL-H | IP Drum | OUTPUT | LOGIC | HRSG.IP.DRUM.LEVEL.H | DERIVED_ALARM
AL-IP-LEVEL-HH | IP Drum | INPUT | vppIPDrumLevelM | LOGIC | value > 1.25 m | 0.5 s
AL-IP-LEVEL-HH | IP Drum | OUTPUT | LOGIC | HRSG.IP.DRUM.LEVEL.HH | DERIVED_ALARM
AL-IP-LEVEL-L | IP Drum | INPUT | vppIPDrumLevelM | LOGIC | value < 0.95 m | 0.5 s
AL-IP-LEVEL-L | IP Drum | OUTPUT | LOGIC | HRSG.IP.DRUM.LEVEL.L | DERIVED_ALARM
AL-IP-LEVEL-LL | IP Drum | INPUT | vppIPDrumLevelM | LOGIC | value < 0.85 m | 0.5 s
AL-IP-LEVEL-LL | IP Drum | OUTPUT | LOGIC | HRSG.IP.DRUM.LEVEL.LL | DERIVED_ALARM
AL-IP-PRESS-L | IP Drum | INPUT | vppIPDrumPressurePa | LOGIC | value < 2550000 Pa | 0.5 s
AL-IP-PRESS-L | IP Drum | OUTPUT | LOGIC | HRSG.IP.DRUM.PRESS.L | DERIVED_ALARM
AL-IP-PRESS-LL | IP Drum | INPUT | vppIPDrumPressurePa | LOGIC | value < 2300000 Pa | 0.5 s
AL-IP-PRESS-LL | IP Drum | OUTPUT | LOGIC | HRSG.IP.DRUM.PRESS.LL | DERIVED_ALARM
AL-IP-FLOW-L | IP Steam Flow | INPUT | vppIPTurbineSteamFlowTH | LOGIC | value < 576 t/h | 0.2 s
AL-IP-FLOW-L | IP Steam Flow | OUTPUT | LOGIC | HRSG.IP.STEAM.FLOW.L | DERIVED_ALARM
AL-IP-FLOW-LL | IP Steam Flow | INPUT | vppIPTurbineSteamFlowTH | LOGIC | value < 378 t/h | 0.2 s
AL-IP-FLOW-LL | IP Steam Flow | OUTPUT | LOGIC | HRSG.IP.STEAM.FLOW.LL | DERIVED_ALARM
AL-LP-LEVEL-H | LP Drum | INPUT | vppLPDrumLevelM | LOGIC | value > 1.85 m | 0.5 s
AL-LP-LEVEL-H | LP Drum | OUTPUT | LOGIC | HRSG.LP.DRUM.LEVEL.H | DERIVED_ALARM
AL-LP-LEVEL-HH | LP Drum | INPUT | vppLPDrumLevelM | LOGIC | value > 1.95 m | 0.5 s
AL-LP-LEVEL-HH | LP Drum | OUTPUT | LOGIC | HRSG.LP.DRUM.LEVEL.HH | DERIVED_ALARM
AL-LP-LEVEL-L | LP Drum | INPUT | vppLPDrumLevelM | LOGIC | value < 1.65 m | 0.5 s
AL-LP-LEVEL-L | LP Drum | OUTPUT | LOGIC | HRSG.LP.DRUM.LEVEL.L | DERIVED_ALARM
AL-LP-LEVEL-LL | LP Drum | INPUT | vppLPDrumLevelM | LOGIC | value < 1.55 m | 0.5 s
AL-LP-LEVEL-LL | LP Drum | OUTPUT | LOGIC | HRSG.LP.DRUM.LEVEL.LL | DERIVED_ALARM
AL-LP-PRESS-L | LP Drum | INPUT | vppLPDrumPressurePa | LOGIC | value < 500000 Pa | 0.5 s
AL-LP-PRESS-L | LP Drum | OUTPUT | LOGIC | HRSG.LP.DRUM.PRESS.L | DERIVED_ALARM
AL-LP-PRESS-LL | LP Drum | INPUT | vppLPDrumPressurePa | LOGIC | value < 450000 Pa | 0.5 s
AL-LP-PRESS-LL | LP Drum | OUTPUT | LOGIC | HRSG.LP.DRUM.PRESS.LL | DERIVED_ALARM
AL-LP-FLOW-L | LP Steam Flow | INPUT | vppLPTurbineSteamFlowTH | LOGIC | value < 630 t/h | 0.2 s
AL-LP-FLOW-L | LP Steam Flow | OUTPUT | LOGIC | HRSG.LP.STEAM.FLOW.L | DERIVED_ALARM
AL-LP-FLOW-LL | LP Steam Flow | INPUT | vppLPTurbineSteamFlowTH | LOGIC | value < 424.8 t/h | 0.2 s
AL-LP-FLOW-LL | LP Steam Flow | OUTPUT | LOGIC | HRSG.LP.STEAM.FLOW.LL | DERIVED_ALARM
PROT-DIRECT-GT | GT Protection | INPUT | vppExternalTripCommandNative | LOGIC | command >= 0.5 | 0 s
PROT-DIRECT-GT | GT Protection | OUTPUT | LOGIC | vppCauseDirectGTTrip | RAW_NODE
PROT-DIRECT-ST | ST Protection | INPUT | vppExternalSTTripCommandNative | LOGIC | command >= 0.5 | 0 s
PROT-DIRECT-ST | ST Protection | OUTPUT | LOGIC | vppCauseDirectSTTrip | RAW_NODE
PROT-GT-BRK-OPEN | GT Protection | INPUT | vppECMS52GTClosedCommandNative | LOGIC | 52GT close command < 0.5 AND GT latch not active | 0 s
PROT-GT-BRK-OPEN | GT Protection | INPUT | vppGTTripLatchInternal | LOGIC | 52GT close command < 0.5 AND GT latch not active | 0 s
PROT-GT-BRK-OPEN | GT Protection | OUTPUT | LOGIC | vppCauseGTBreakerOpenWhileRunning | RAW_NODE
PROT-HP-DRUM-HH | HP Drum Protection | INPUT | vppHPDrumHHRaw | LOGIC | raw HH state == 1 | runtime-defined
PROT-HP-DRUM-HH | HP Drum Protection | OUTPUT | LOGIC | vppCauseHPDrumHH | RAW_NODE
PROT-HP-DRUM-LL | HP Drum Protection | INPUT | vppHPDrumLLRaw | LOGIC | raw LL state == 1 | runtime-defined
PROT-HP-DRUM-LL | HP Drum Protection | OUTPUT | LOGIC | vppCauseHPDrumLL | RAW_NODE
PROT-IP-DRUM-HH | IP Drum Protection | INPUT | vppIPDrumHHRaw | LOGIC | raw HH state == 1 | runtime-defined
PROT-IP-DRUM-HH | IP Drum Protection | OUTPUT | LOGIC | vppCauseIPDrumHH | RAW_NODE
PROT-IP-DRUM-LL | IP Drum Protection | INPUT | vppIPDrumLLRaw | LOGIC | raw LL state == 1 | runtime-defined
PROT-IP-DRUM-LL | IP Drum Protection | OUTPUT | LOGIC | vppCauseIPDrumLL | RAW_NODE
PROT-LP-DRUM-HH | LP Drum Protection | INPUT | vppLPDrumHHRaw | LOGIC | raw HH state == 1 | runtime-defined
PROT-LP-DRUM-HH | LP Drum Protection | OUTPUT | LOGIC | vppCauseLPDrumHH | RAW_NODE
PROT-LP-DRUM-LL | LP Drum Protection | INPUT | vppLPDrumLLRaw | LOGIC | raw LL state == 1 | runtime-defined
PROT-LP-DRUM-LL | LP Drum Protection | OUTPUT | LOGIC | vppCauseLPDrumLL | RAW_NODE
PROT-GT-REQUEST | GT Protection | INPUT | vppCauseDirectGTTrip | LOGIC | OR(all inputs) | 0 s
PROT-GT-REQUEST | GT Protection | INPUT | vppCauseGTBreakerOpenWhileRunning | LOGIC | OR(all inputs) | 0 s
PROT-GT-REQUEST | GT Protection | INPUT | vppCauseHPDrumLL | LOGIC | OR(all inputs) | 0 s
PROT-GT-REQUEST | GT Protection | INPUT | vppCauseIPDrumLL | LOGIC | OR(all inputs) | 0 s
PROT-GT-REQUEST | GT Protection | INPUT | vppCauseLPDrumLL | LOGIC | OR(all inputs) | 0 s
PROT-GT-REQUEST | GT Protection | OUTPUT | LOGIC | vppGTTripRequest | RAW_NODE
PROT-ST-REQUEST | ST Protection | INPUT | vppCauseDirectGTTrip | LOGIC | OR(all 9 causes) | 0 s
PROT-ST-REQUEST | ST Protection | INPUT | vppCauseDirectSTTrip | LOGIC | OR(all 9 causes) | 0 s
PROT-ST-REQUEST | ST Protection | INPUT | vppCauseGTBreakerOpenWhileRunning | LOGIC | OR(all 9 causes) | 0 s
PROT-ST-REQUEST | ST Protection | INPUT | vppCauseHPDrumHH | LOGIC | OR(all 9 causes) | 0 s
PROT-ST-REQUEST | ST Protection | INPUT | vppCauseIPDrumHH | LOGIC | OR(all 9 causes) | 0 s
PROT-ST-REQUEST | ST Protection | INPUT | vppCauseLPDrumHH | LOGIC | OR(all 9 causes) | 0 s
PROT-ST-REQUEST | ST Protection | INPUT | vppCauseHPDrumLL | LOGIC | OR(all 9 causes) | 0 s
PROT-ST-REQUEST | ST Protection | INPUT | vppCauseIPDrumLL | LOGIC | OR(all 9 causes) | 0 s
PROT-ST-REQUEST | ST Protection | INPUT | vppCauseLPDrumLL | LOGIC | OR(all 9 causes) | 0 s
PROT-ST-REQUEST | ST Protection | OUTPUT | LOGIC | vppSTTripRequest | RAW_NODE
PROT-GT-LATCH | GT Protection | INPUT | vppGTTripRequest | LOGIC | request=1 AND reset<0.5 -> latch; reset clears | event-driven
PROT-GT-LATCH | GT Protection | INPUT | vppGTTripResetNative | LOGIC | request=1 AND reset<0.5 -> latch; reset clears | event-driven
PROT-GT-LATCH | GT Protection | OUTPUT | LOGIC | vppGTTripLatch | RAW_NODE
PROT-ST-LATCH | ST Protection | INPUT | vppSTTripRequest | LOGIC | request=1 AND reset<0.5 -> latch; reset clears | event-driven
PROT-ST-LATCH | ST Protection | INPUT | vppSTTripResetNative | LOGIC | request=1 AND reset<0.5 -> latch; reset clears | event-driven
PROT-ST-LATCH | ST Protection | OUTPUT | LOGIC | vppSTTripLatchPublished | RAW_NODE
SEQ-52GT-TRIPCMD | GT Protection | INPUT | vppGTTripLatch | LOGIC | GT latch active | 0.055 s
SEQ-52GT-TRIPCMD | GT Protection | OUTPUT | LOGIC | vpp52GTTripCmd | RAW_NODE
SEQ-52GT-OPEN | GT Protection | INPUT | vppGTTripLatch | LOGIC | GT latch active -> breaker opens | 0.080 s
SEQ-52GT-OPEN | GT Protection | INPUT | vppECMS52GTClosedCommandNative | LOGIC | GT latch active -> breaker opens | 0.080 s
SEQ-52GT-OPEN | GT Protection | OUTPUT | LOGIC | vpp52GTClosed | RAW_NODE
SEQ-52ST-TRIPCMD | ST Protection | INPUT | vppSTTripLatchPublished | LOGIC | ST latch active | 0 s
SEQ-52ST-TRIPCMD | ST Protection | OUTPUT | LOGIC | vpp52STTripCmd | RAW_NODE
SEQ-52ST-OPEN | ST Protection | INPUT | vppSTTripLatchPublished | LOGIC | ST latch active -> breaker opens | 0.100 s
SEQ-52ST-OPEN | ST Protection | INPUT | vppECMS52STClosedCommandNative | LOGIC | ST latch active -> breaker opens | 0.100 s
SEQ-52ST-OPEN | ST Protection | OUTPUT | LOGIC | vpp52STClosed | RAW_NODE
RESP-GT-POWER | GT Response | INPUT | vpp52GTClosed | LOGIC | if 52GT not closed then GT generator power = 0 | immediate model relation
RESP-GT-POWER | GT Response | OUTPUT | LOGIC | vppGTGPowerMW | RAW_NODE
RESP-GT-SPEED | GT Response | INPUT | vpp52GTClosed | LOGIC | if 52GT opens, speed decays from nominal by coastdown model | dynamic
RESP-GT-SPEED | GT Response | OUTPUT | LOGIC | vppGTGSpeedRPM | RAW_NODE
CMD-FWP-HP-TRIP | FWP HP | INPUT | vppHPFWPTripPushbuttonNative | LOGIC | operator/test PB writes trip command through runtime interface | external runtime interface
CMD-FWP-HP-TRIP | FWP HP | OUTPUT | LOGIC | vppHPFWPTripCommandNative | RAW_NODE
CMD-FWP-HP-TRIP | FWP HP | OUTPUT | LOGIC | vppHPFWPTripLatchNative | RAW_NODE
CMD-FWP-HP-TRIP | FWP HP | OUTPUT | LOGIC | vppVCBA01TripCommandNative | RAW_NODE
CMD-FWP-HP-RESET | FWP HP | INPUT | vppHPFWPResetPushbuttonNative | LOGIC | operator/test reset PB | external runtime interface
CMD-FWP-HP-RESET | FWP HP | OUTPUT | LOGIC | vppHPFWPTripLatchNative | RAW_NODE
CMD-FWP-IP-TRIP | FWP IP | INPUT | vppIPFWPTripPushbuttonNative | LOGIC | operator/test PB writes trip command through runtime interface | external runtime interface
CMD-FWP-IP-TRIP | FWP IP | OUTPUT | LOGIC | vppIPFWPTripCommandNative | RAW_NODE
CMD-FWP-IP-TRIP | FWP IP | OUTPUT | LOGIC | vppIPFWPTripLatchNative | RAW_NODE
CMD-FWP-IP-TRIP | FWP IP | OUTPUT | LOGIC | vppVCBB01TripCommandNative | RAW_NODE
CMD-FWP-IP-RESET | FWP IP | INPUT | vppIPFWPResetPushbuttonNative | LOGIC | operator/test reset PB | external runtime interface
CMD-FWP-IP-RESET | FWP IP | OUTPUT | LOGIC | vppIPFWPTripLatchNative | RAW_NODE
CMD-FWP-LP-TRIP | FWP LP | INPUT | vppLPFWPTripPushbuttonNative | LOGIC | operator/test PB writes trip command through runtime interface | external runtime interface
CMD-FWP-LP-TRIP | FWP LP | OUTPUT | LOGIC | vppLPFWPTripCommandNative | RAW_NODE
CMD-FWP-LP-TRIP | FWP LP | OUTPUT | LOGIC | vppLPFWPTripLatchNative | RAW_NODE
CMD-FWP-LP-TRIP | FWP LP | OUTPUT | LOGIC | vppVCBA02TripCommandNative | RAW_NODE
CMD-FWP-LP-RESET | FWP LP | INPUT | vppLPFWPResetPushbuttonNative | LOGIC | operator/test reset PB | external runtime interface
CMD-FWP-LP-RESET | FWP LP | OUTPUT | LOGIC | vppLPFWPTripLatchNative | RAW_NODE

## 03_Group_View
group | rule_count | rule_ids | primary_inputs | primary_outputs
GT Exhaust | 4 | AL-GT-FLOW-L; AL-GT-FLOW-LL; AL-GT-TEMP-L; AL-GT-TEMP-LL | vppGTExhaustMassFlowState; vppGTExhaustTemperatureK | GT.EXHAUST.FLOW.L; GT.EXHAUST.FLOW.LL; GT.EXHAUST.TEMP.L; GT.EXHAUST.TEMP.LL
HP Drum | 6 | AL-HP-LEVEL-H; AL-HP-LEVEL-HH; AL-HP-LEVEL-L; AL-HP-LEVEL-LL; AL-HP-PRESS-L; AL-HP-PRESS-LL | vppHPDrumLevelM; vppHPDrumPressurePa | HRSG.HP.DRUM.LEVEL.H; HRSG.HP.DRUM.LEVEL.HH; HRSG.HP.DRUM.LEVEL.L; HRSG.HP.DRUM.LEVEL.LL; HRSG.HP.DRUM.PRESS.L; HRSG.HP.DRUM.PRESS.LL
HP Steam Flow | 2 | AL-HP-FLOW-L; AL-HP-FLOW-LL | vppHPTurbineSteamFlowTH | HRSG.HP.STEAM.FLOW.L; HRSG.HP.STEAM.FLOW.LL
IP Drum | 6 | AL-IP-LEVEL-H; AL-IP-LEVEL-HH; AL-IP-LEVEL-L; AL-IP-LEVEL-LL; AL-IP-PRESS-L; AL-IP-PRESS-LL | vppIPDrumLevelM; vppIPDrumPressurePa | HRSG.IP.DRUM.LEVEL.H; HRSG.IP.DRUM.LEVEL.HH; HRSG.IP.DRUM.LEVEL.L; HRSG.IP.DRUM.LEVEL.LL; HRSG.IP.DRUM.PRESS.L; HRSG.IP.DRUM.PRESS.LL
IP Steam Flow | 2 | AL-IP-FLOW-L; AL-IP-FLOW-LL | vppIPTurbineSteamFlowTH | HRSG.IP.STEAM.FLOW.L; HRSG.IP.STEAM.FLOW.LL
LP Drum | 6 | AL-LP-LEVEL-H; AL-LP-LEVEL-HH; AL-LP-LEVEL-L; AL-LP-LEVEL-LL; AL-LP-PRESS-L; AL-LP-PRESS-LL | vppLPDrumLevelM; vppLPDrumPressurePa | HRSG.LP.DRUM.LEVEL.H; HRSG.LP.DRUM.LEVEL.HH; HRSG.LP.DRUM.LEVEL.L; HRSG.LP.DRUM.LEVEL.LL; HRSG.LP.DRUM.PRESS.L; HRSG.LP.DRUM.PRESS.LL
LP Steam Flow | 2 | AL-LP-FLOW-L; AL-LP-FLOW-LL | vppLPTurbineSteamFlowTH | HRSG.LP.STEAM.FLOW.L; HRSG.LP.STEAM.FLOW.LL
GT Protection | 6 | PROT-DIRECT-GT; PROT-GT-BRK-OPEN; PROT-GT-REQUEST; PROT-GT-LATCH; SEQ-52GT-TRIPCMD; SEQ-52GT-OPEN | vppCauseDirectGTTrip; vppCauseGTBreakerOpenWhileRunning; vppCauseHPDrumLL; vppCauseIPDrumLL; vppCauseLPDrumLL; vppECMS52GTClosedCommandNative; vppExternalTripCommandNative; vppGTTripLatch; vppGTTripLatchInternal; vppGTTripRequest; vppGTTripResetNative | vpp52GTClosed; vpp52GTTripCmd; vppCauseDirectGTTrip; vppCauseGTBreakerOpenWhileRunning; vppGTTripLatch; vppGTTripRequest
ST Protection | 5 | PROT-DIRECT-ST; PROT-ST-REQUEST; PROT-ST-LATCH; SEQ-52ST-TRIPCMD; SEQ-52ST-OPEN | vppCauseDirectGTTrip; vppCauseDirectSTTrip; vppCauseGTBreakerOpenWhileRunning; vppCauseHPDrumHH; vppCauseHPDrumLL; vppCauseIPDrumHH; vppCauseIPDrumLL; vppCauseLPDrumHH; vppCauseLPDrumLL; vppECMS52STClosedCommandNative; vppExternalSTTripCommandNative; vppSTTripLatchPublished; vppSTTripRequest; vppSTTripResetNative | vpp52STClosed; vpp52STTripCmd; vppCauseDirectSTTrip; vppSTTripLatchPublished; vppSTTripRequest
HP Drum Protection | 2 | PROT-HP-DRUM-HH; PROT-HP-DRUM-LL | vppHPDrumHHRaw; vppHPDrumLLRaw | vppCauseHPDrumHH; vppCauseHPDrumLL
IP Drum Protection | 2 | PROT-IP-DRUM-HH; PROT-IP-DRUM-LL | vppIPDrumHHRaw; vppIPDrumLLRaw | vppCauseIPDrumHH; vppCauseIPDrumLL
LP Drum Protection | 2 | PROT-LP-DRUM-HH; PROT-LP-DRUM-LL | vppLPDrumHHRaw; vppLPDrumLLRaw | vppCauseLPDrumHH; vppCauseLPDrumLL
GT Response | 2 | RESP-GT-POWER; RESP-GT-SPEED | vpp52GTClosed | vppGTGPowerMW; vppGTGSpeedRPM
FWP HP | 2 | CMD-FWP-HP-TRIP; CMD-FWP-HP-RESET | vppHPFWPResetPushbuttonNative; vppHPFWPTripPushbuttonNative | vppHPFWPTripCommandNative; vppHPFWPTripLatchNative; vppVCBA01TripCommandNative
FWP IP | 2 | CMD-FWP-IP-TRIP; CMD-FWP-IP-RESET | vppIPFWPResetPushbuttonNative; vppIPFWPTripPushbuttonNative | vppIPFWPTripCommandNative; vppIPFWPTripLatchNative; vppVCBB01TripCommandNative
FWP LP | 2 | CMD-FWP-LP-TRIP; CMD-FWP-LP-RESET | vppLPFWPResetPushbuttonNative; vppLPFWPTripPushbuttonNative | vppLPFWPTripCommandNative; vppLPFWPTripLatchNative; vppVCBA02TripCommandNative

## 04_Source_Notes
Source / Rule | Use
Run #41 | Behavior evidence only; not an identity naming source.
RAW / OPC UA | Every Current input node must be an exact RAW-observed or source-confirmed node.
Derived output | Alarm/output IDs may be TripLens-local derived IDs and must be labelled NOT_OPCUA_NODE.
Canonical/display aliases | Readable local aliases do not prove OPC UA existence.
Scenario Lab | Lab-only inputs are excluded from Operational Logic.
Blind boundary | Scenario/preset/expected cause/test audit are excluded from analyzer input.
Primary-cause gate | A later post-trip cause cannot be promoted to initiating Primary Cause.

## 01_Logic_Master_Grouped
input_group_id | input_signature | branch_count | branch_index | rule_id | group | logic_name | logic_type | input_nodes | condition | delay | reset_hysteresis | output_nodes_or_tags | output_class | validation_status | source_basis | notes | run41_status | release_status | run41_evidence_scenarios | run41_evidence_note | input_identity_status | output_identity_status | hallucination_audit_status | live_input_status | live_output_status | live_validation_run | live_validation_note
IG-001 | vppGTExhaustMassFlowState | 2 | 1 | AL-GT-FLOW-L | GT Exhaust | GT exhaust flow low | ALARM | vppGTExhaustMassFlowState | value < 545 kg/s | 0.2 s | +6 kg/s | GT.EXHAUST.FLOW.L | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW input node exists |  | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-001 | vppGTExhaustMassFlowState | 2 | 2 | AL-GT-FLOW-LL | GT Exhaust | GT exhaust flow low-low | ALARM | vppGTExhaustMassFlowState | value < 300 kg/s | 0.2 s | +6 kg/s | GT.EXHAUST.FLOW.LL | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW input node exists |  | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-002 | vppGTExhaustTemperatureK | 2 | 1 | AL-GT-TEMP-L | GT Exhaust | GT exhaust temperature low | ALARM | vppGTExhaustTemperatureK | value < 805 K | 0.2 s | +5 K | GT.EXHAUST.TEMP.L | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW input node exists |  | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-002 | vppGTExhaustTemperatureK | 2 | 2 | AL-GT-TEMP-LL | GT Exhaust | GT exhaust temperature low-low | ALARM | vppGTExhaustTemperatureK | value < 580 K | 0.2 s | +5 K | GT.EXHAUST.TEMP.LL | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW input node exists |  | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-003 | vppHPDrumLevelM | 4 | 1 | AL-HP-LEVEL-H | HP Drum | HP drum level H | ALARM | vppHPDrumLevelM | value > 1.15 m | 0.5 s | 0.02 m | HRSG.HP.DRUM.LEVEL.H | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW input node exists |  | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-003 | vppHPDrumLevelM | 4 | 2 | AL-HP-LEVEL-HH | HP Drum | HP drum level HH | ALARM | vppHPDrumLevelM | value > 1.25 m | 0.5 s | 0.02 m | HRSG.HP.DRUM.LEVEL.HH | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW input node exists |  | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-003 | vppHPDrumLevelM | 4 | 3 | AL-HP-LEVEL-L | HP Drum | HP drum level L | ALARM | vppHPDrumLevelM | value < 0.95 m | 0.5 s | 0.02 m | HRSG.HP.DRUM.LEVEL.L | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW input node exists |  | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-003 | vppHPDrumLevelM | 4 | 4 | AL-HP-LEVEL-LL | HP Drum | HP drum level LL | ALARM | vppHPDrumLevelM | value < 0.85 m | 0.5 s | 0.02 m | HRSG.HP.DRUM.LEVEL.LL | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW input node exists |  | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-004 | vppHPDrumPressurePa | 2 | 1 | AL-HP-PRESS-L | HP Drum | HP drum pressure L | ALARM | vppHPDrumPressurePa | value < 12000000 Pa | 0.5 s | 200000 Pa | HRSG.HP.DRUM.PRESS.L | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW input node exists |  | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-004 | vppHPDrumPressurePa | 2 | 2 | AL-HP-PRESS-LL | HP Drum | HP drum pressure LL | ALARM | vppHPDrumPressurePa | value < 10800000 Pa | 0.5 s | 200000 Pa | HRSG.HP.DRUM.PRESS.LL | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW input node exists |  | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-005 | vppHPTurbineSteamFlowTH | 2 | 1 | AL-HP-FLOW-L | HP Steam Flow | HP turbine steam flow L | ALARM | vppHPTurbineSteamFlowTH | value < 486 t/h | 0.2 s | 10.8 t/h | HRSG.HP.STEAM.FLOW.L | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW node is vpp*TurbineSteamFlowTH; threshold converted exactly from kg/s × 3.6 |  | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-005 | vppHPTurbineSteamFlowTH | 2 | 2 | AL-HP-FLOW-LL | HP Steam Flow | HP turbine steam flow LL | ALARM | vppHPTurbineSteamFlowTH | value < 324 t/h | 0.2 s | 10.8 t/h | HRSG.HP.STEAM.FLOW.LL | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW node is vpp*TurbineSteamFlowTH; threshold converted exactly from kg/s × 3.6 |  | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-006 | vppIPDrumLevelM | 4 | 1 | AL-IP-LEVEL-H | IP Drum | IP drum level H | ALARM | vppIPDrumLevelM | value > 1.15 m | 0.5 s | 0.02 m | HRSG.IP.DRUM.LEVEL.H | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW input node exists |  | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-006 | vppIPDrumLevelM | 4 | 2 | AL-IP-LEVEL-HH | IP Drum | IP drum level HH | ALARM | vppIPDrumLevelM | value > 1.25 m | 0.5 s | 0.02 m | HRSG.IP.DRUM.LEVEL.HH | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW input node exists |  | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-006 | vppIPDrumLevelM | 4 | 3 | AL-IP-LEVEL-L | IP Drum | IP drum level L | ALARM | vppIPDrumLevelM | value < 0.95 m | 0.5 s | 0.02 m | HRSG.IP.DRUM.LEVEL.L | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW input node exists |  | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-006 | vppIPDrumLevelM | 4 | 4 | AL-IP-LEVEL-LL | IP Drum | IP drum level LL | ALARM | vppIPDrumLevelM | value < 0.85 m | 0.5 s | 0.02 m | HRSG.IP.DRUM.LEVEL.LL | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW input node exists |  | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-007 | vppIPDrumPressurePa | 2 | 1 | AL-IP-PRESS-L | IP Drum | IP drum pressure L | ALARM | vppIPDrumPressurePa | value < 2550000 Pa | 0.5 s | 50000 Pa | HRSG.IP.DRUM.PRESS.L | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW input node exists |  | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-007 | vppIPDrumPressurePa | 2 | 2 | AL-IP-PRESS-LL | IP Drum | IP drum pressure LL | ALARM | vppIPDrumPressurePa | value < 2300000 Pa | 0.5 s | 50000 Pa | HRSG.IP.DRUM.PRESS.LL | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW input node exists |  | RUN41_BOUND_NOT_TRIGGERED | RC_BOUND_ONLY |  | Rule/source bound in Run #41, but no ACTIVE event was observed. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-008 | vppIPTurbineSteamFlowTH | 2 | 1 | AL-IP-FLOW-L | IP Steam Flow | IP turbine steam flow L | ALARM | vppIPTurbineSteamFlowTH | value < 576 t/h | 0.2 s | 10.8 t/h | HRSG.IP.STEAM.FLOW.L | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW node is vpp*TurbineSteamFlowTH; threshold converted exactly from kg/s × 3.6 |  | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-008 | vppIPTurbineSteamFlowTH | 2 | 2 | AL-IP-FLOW-LL | IP Steam Flow | IP turbine steam flow LL | ALARM | vppIPTurbineSteamFlowTH | value < 378 t/h | 0.2 s | 10.8 t/h | HRSG.IP.STEAM.FLOW.LL | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW node is vpp*TurbineSteamFlowTH; threshold converted exactly from kg/s × 3.6 |  | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-009 | vppLPDrumLevelM | 4 | 1 | AL-LP-LEVEL-H | LP Drum | LP drum level H | ALARM | vppLPDrumLevelM | value > 1.85 m | 0.5 s | 0.02 m | HRSG.LP.DRUM.LEVEL.H | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW input node exists |  | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-009 | vppLPDrumLevelM | 4 | 2 | AL-LP-LEVEL-HH | LP Drum | LP drum level HH | ALARM | vppLPDrumLevelM | value > 1.95 m | 0.5 s | 0.02 m | HRSG.LP.DRUM.LEVEL.HH | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW input node exists |  | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-009 | vppLPDrumLevelM | 4 | 3 | AL-LP-LEVEL-L | LP Drum | LP drum level L | ALARM | vppLPDrumLevelM | value < 1.65 m | 0.5 s | 0.02 m | HRSG.LP.DRUM.LEVEL.L | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW input node exists |  | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-009 | vppLPDrumLevelM | 4 | 4 | AL-LP-LEVEL-LL | LP Drum | LP drum level LL | ALARM | vppLPDrumLevelM | value < 1.55 m | 0.5 s | 0.02 m | HRSG.LP.DRUM.LEVEL.LL | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW input node exists |  | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-010 | vppLPDrumPressurePa | 2 | 1 | AL-LP-PRESS-L | LP Drum | LP drum pressure L | ALARM | vppLPDrumPressurePa | value < 500000 Pa | 0.5 s | 10000 Pa | HRSG.LP.DRUM.PRESS.L | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW input node exists |  | RUN41_BOUND_NOT_TRIGGERED | RC_BOUND_ONLY |  | Rule/source bound in Run #41, but no ACTIVE event was observed. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-010 | vppLPDrumPressurePa | 2 | 2 | AL-LP-PRESS-LL | LP Drum | LP drum pressure LL | ALARM | vppLPDrumPressurePa | value < 450000 Pa | 0.5 s | 10000 Pa | HRSG.LP.DRUM.PRESS.LL | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW input node exists |  | RUN41_BOUND_NOT_TRIGGERED | RC_BOUND_ONLY |  | Rule/source bound in Run #41, but no ACTIVE event was observed. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-011 | vppLPTurbineSteamFlowTH | 2 | 1 | AL-LP-FLOW-L | LP Steam Flow | LP turbine steam flow L | ALARM | vppLPTurbineSteamFlowTH | value < 630 t/h | 0.2 s | 10.8 t/h | HRSG.LP.STEAM.FLOW.L | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW node is vpp*TurbineSteamFlowTH; threshold converted exactly from kg/s × 3.6 |  | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-011 | vppLPTurbineSteamFlowTH | 2 | 2 | AL-LP-FLOW-LL | LP Steam Flow | LP turbine steam flow LL | ALARM | vppLPTurbineSteamFlowTH | value < 424.8 t/h | 0.2 s | 10.8 t/h | HRSG.LP.STEAM.FLOW.LL | DERIVED_ALARM | PARTIAL | Current DCS alarm rule; RAW node is vpp*TurbineSteamFlowTH; threshold converted exactly from kg/s × 3.6 |  | RUN41_PROVEN_TRIGGERED | RC_CONFIRMED | Run #41 passing scenarios | Alarm ACTIVE was observed in at least one passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | LOCAL_DERIVED_OUTPUT_ONLY | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-012 | vppExternalTripCommandNative | 1 | 1 | PROT-DIRECT-GT | GT Protection | Direct GT trip cause | PROTECTION_CAUSE | vppExternalTripCommandNative | command >= 0.5 | 0 s | reset by GT reset | vppCauseDirectGTTrip | RAW_NODE | PASS | RAW node + runtime regression evidence |  | RUN41_PROVEN_ASSERTED | RC_CONFIRMED | direct_gt | Protection cause asserted in a passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-013 | vppExternalSTTripCommandNative | 1 | 1 | PROT-DIRECT-ST | ST Protection | Direct ST trip cause | PROTECTION_CAUSE | vppExternalSTTripCommandNative | command >= 0.5 | 0 s | reset by ST reset | vppCauseDirectSTTrip | RAW_NODE | PASS | RAW node + runtime regression evidence |  | RUN41_PROVEN_ASSERTED | RC_CONFIRMED | direct_st | Protection cause asserted in a passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-014 | vppECMS52GTClosedCommandNative ¦ vppGTTripLatchInternal | 1 | 1 | PROT-GT-BRK-OPEN | GT Protection | GT breaker open while running cause | PROTECTION_CAUSE | vppECMS52GTClosedCommandNative ¦ vppGTTripLatchInternal | 52GT close command < 0.5 AND GT latch not active | 0 s | state reset | vppCauseGTBreakerOpenWhileRunning | RAW_NODE | PARTIAL | Exact expression recovered from model compile trace |  | RUN41_PROVEN_ASSERTED | RC_CONFIRMED | gt_breaker | Protection cause asserted in a passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-015 | vppHPDrumHHRaw | 1 | 1 | PROT-HP-DRUM-HH | HP Drum Protection | HP drum HH protection cause | PROTECTION_CAUSE | vppHPDrumHHRaw | raw HH state == 1 | runtime-defined | reset/return per runtime | vppCauseHPDrumHH | RAW_NODE | PARTIAL | RAW comparator/cause nodes exist; exact internal debounce retained in runtime |  | RUN41_PROVEN_ASSERTED | RC_CONFIRMED | hp_drum_hh | Protection cause asserted in a passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-016 | vppHPDrumLLRaw | 1 | 1 | PROT-HP-DRUM-LL | HP Drum Protection | HP drum LL protection cause | PROTECTION_CAUSE | vppHPDrumLLRaw | raw LL state == 1 | runtime-defined | reset/return per runtime | vppCauseHPDrumLL | RAW_NODE | PARTIAL | RAW comparator/cause nodes exist; exact internal debounce retained in runtime |  | RUN41_PROVEN_ASSERTED | RC_CONFIRMED | hp_drum_ll | Protection cause asserted in a passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-017 | vppIPDrumHHRaw | 1 | 1 | PROT-IP-DRUM-HH | IP Drum Protection | IP drum HH protection cause | PROTECTION_CAUSE | vppIPDrumHHRaw | raw HH state == 1 | runtime-defined | reset/return per runtime | vppCauseIPDrumHH | RAW_NODE | PARTIAL | RAW comparator/cause nodes exist; exact internal debounce retained in runtime |  | RUN41_PROVEN_ASSERTED | RC_CONFIRMED | ip_drum_hh | Protection cause asserted in a passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-018 | vppIPDrumLLRaw | 1 | 1 | PROT-IP-DRUM-LL | IP Drum Protection | IP drum LL protection cause | PROTECTION_CAUSE | vppIPDrumLLRaw | raw LL state == 1 | runtime-defined | reset/return per runtime | vppCauseIPDrumLL | RAW_NODE | PARTIAL | RAW comparator/cause nodes exist; exact internal debounce retained in runtime |  | RUN41_PROVEN_ASSERTED | RC_CONFIRMED | ip_drum_ll | Protection cause asserted in a passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-019 | vppLPDrumHHRaw | 1 | 1 | PROT-LP-DRUM-HH | LP Drum Protection | LP drum HH protection cause | PROTECTION_CAUSE | vppLPDrumHHRaw | raw HH state == 1 | runtime-defined | reset/return per runtime | vppCauseLPDrumHH | RAW_NODE | PARTIAL | RAW comparator/cause nodes exist; exact internal debounce retained in runtime |  | RUN41_PROVEN_ASSERTED | RC_CONFIRMED | lp_drum_hh | Protection cause asserted in a passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-020 | vppLPDrumLLRaw | 1 | 1 | PROT-LP-DRUM-LL | LP Drum Protection | LP drum LL protection cause | PROTECTION_CAUSE | vppLPDrumLLRaw | raw LL state == 1 | runtime-defined | reset/return per runtime | vppCauseLPDrumLL | RAW_NODE | PARTIAL | RAW comparator/cause nodes exist; exact internal debounce retained in runtime |  | RUN41_PROVEN_ASSERTED | RC_CONFIRMED | lp_drum_ll | Protection cause asserted in a passing Run #41 scenario. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-021 | vppCauseDirectGTTrip ¦ vppCauseGTBreakerOpenWhileRunning ¦ vppCauseHPDrumLL ¦ vppCauseIPDrumLL ¦ vppCauseLPDrumLL | 1 | 1 | PROT-GT-REQUEST | GT Protection | GT trip request OR matrix | TRIP_REQUEST | vppCauseDirectGTTrip ¦ vppCauseGTBreakerOpenWhileRunning ¦ vppCauseHPDrumLL ¦ vppCauseIPDrumLL ¦ vppCauseLPDrumLL | OR(all inputs) | 0 s | GT reset | vppGTTripRequest | RAW_NODE | PASS | Exact GT request equation recovered from model compile trace |  | RUN41_PROVEN | RC_CONFIRMED | direct_gt | Observed in Run #41 direct_gt RAW/EVENT chain. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-022 | vppCauseDirectGTTrip ¦ vppCauseDirectSTTrip ¦ vppCauseGTBreakerOpenWhileRunning ¦ vppCauseHPDrumHH ¦ vppCauseHPDrumLL ¦ vppCauseIPDrumHH ¦ vppCauseIPDrumLL ¦ vppCauseLPDrumHH ¦ vppCauseLPDrumLL | 1 | 1 | PROT-ST-REQUEST | ST Protection | ST trip request common-trip matrix | TRIP_REQUEST | vppCauseDirectGTTrip ¦ vppCauseDirectSTTrip ¦ vppCauseGTBreakerOpenWhileRunning ¦ vppCauseHPDrumHH ¦ vppCauseIPDrumHH ¦ vppCauseLPDrumHH ¦ vppCauseHPDrumLL ¦ vppCauseIPDrumLL ¦ vppCauseLPDrumLL | OR(all 9 causes) | 0 s | ST reset | vppSTTripRequest | RAW_NODE | PASS | 9-cause common-trip matrix + RAW nodes |  | RUN41_PROVEN | RC_CONFIRMED | direct_gt | Observed in Run #41 direct_gt RAW/EVENT chain. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-023 | vppGTTripRequest ¦ vppGTTripResetNative | 1 | 1 | PROT-GT-LATCH | GT Protection | GT trip latch | LATCH | vppGTTripRequest ¦ vppGTTripResetNative | request=1 AND reset<0.5 -> latch; reset clears | event-driven | reset input | vppGTTripLatch | RAW_NODE | PASS | Runtime latch node and request/reset nodes exist |  | RUN41_PROVEN | RC_CONFIRMED | direct_gt | Observed in Run #41 direct_gt RAW/EVENT chain. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-024 | vppSTTripRequest ¦ vppSTTripResetNative | 1 | 1 | PROT-ST-LATCH | ST Protection | ST trip latch | LATCH | vppSTTripRequest ¦ vppSTTripResetNative | request=1 AND reset<0.5 -> latch; reset clears | event-driven | reset input | vppSTTripLatchPublished | RAW_NODE | PASS | Runtime latch node and request/reset nodes exist |  | RUN41_PROVEN | RC_CONFIRMED | direct_gt | Observed in Run #41 direct_gt RAW/EVENT chain. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-025 | vppGTTripLatch | 1 | 1 | SEQ-52GT-TRIPCMD | GT Protection | 52GT trip command timing | BREAKER_SEQUENCE | vppGTTripLatch | GT latch active | 0.055 s | - | vpp52GTTripCmd | RAW_NODE | PASS | vppGTTripCommandDelay = 0.055 s |  | RUN41_PROVEN | RC_CONFIRMED | direct_gt | Observed in Run #41 direct_gt RAW/EVENT chain. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-026 | vppECMS52GTClosedCommandNative ¦ vppGTTripLatch | 1 | 1 | SEQ-52GT-OPEN | GT Protection | 52GT breaker open timing | BREAKER_SEQUENCE | vppGTTripLatch ¦ vppECMS52GTClosedCommandNative | GT latch active -> breaker opens | 0.080 s | - | vpp52GTClosed | RAW_NODE | PASS | vppGTBreakerOpenDelay = 0.080 s; EVENT run observed 48.44 -> 48.520005 |  | RUN41_PROVEN | RC_CONFIRMED | direct_gt | Observed in Run #41 direct_gt RAW/EVENT chain. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-027 | vppSTTripLatchPublished | 1 | 1 | SEQ-52ST-TRIPCMD | ST Protection | 52ST trip command | BREAKER_SEQUENCE | vppSTTripLatchPublished | ST latch active | 0 s | - | vpp52STTripCmd | RAW_NODE | PASS | Runtime node sequence |  | RUN41_PROVEN | RC_CONFIRMED | direct_gt | Observed in Run #41 direct_gt RAW/EVENT chain. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-028 | vppECMS52STClosedCommandNative ¦ vppSTTripLatchPublished | 1 | 1 | SEQ-52ST-OPEN | ST Protection | 52ST breaker open timing | BREAKER_SEQUENCE | vppSTTripLatchPublished ¦ vppECMS52STClosedCommandNative | ST latch active -> breaker opens | 0.100 s | - | vpp52STClosed | RAW_NODE | PASS | vppSTBreakerOpenDelay = 0.100 s; EVENT run observed 48.44 -> 48.540005 |  | RUN41_PROVEN | RC_CONFIRMED | direct_gt | Observed in Run #41 direct_gt RAW/EVENT chain. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-029 | vpp52GTClosed | 2 | 1 | RESP-GT-POWER | GT Response | GT power response after breaker open | PHYSICAL_RESPONSE | vpp52GTClosed | if 52GT not closed then GT generator power = 0 | immediate model relation | - | vppGTGPowerMW | RAW_NODE | PASS | Exact model equation |  | RUN41_PROVEN | RC_CONFIRMED | direct_gt | Observed in Run #41 direct_gt RAW/EVENT chain. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-029 | vpp52GTClosed | 2 | 2 | RESP-GT-SPEED | GT Response | GT speed coastdown after breaker open | PHYSICAL_RESPONSE | vpp52GTClosed | if 52GT opens, speed decays from nominal by coastdown model | dynamic | - | vppGTGSpeedRPM | RAW_NODE | PASS | Exact model equation |  | RUN41_PROVEN | RC_CONFIRMED | direct_gt | Observed in Run #41 direct_gt RAW/EVENT chain. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-030 | vppHPFWPTripPushbuttonNative | 1 | 1 | CMD-FWP-HP-TRIP | FWP HP | HP FWP trip command interface | COMMAND_INTERFACE | vppHPFWPTripPushbuttonNative | operator/test PB writes trip command through runtime interface | external runtime interface | reset PB | vppHPFWPTripCommandNative ¦ vppHPFWPTripLatchNative ¦ vppVCBA01TripCommandNative | RAW_NODE | PARTIAL | All command/latch/breaker nodes exist in RAW; exact client-side sequencing is not re-invented here |  | RUN41_FAILED_NOT_PROVEN | RC_NOT_CONFIRMED | hp_bfp | Run #41 hp_bfp did not prove latch/breaker/physical trip chain before model stall. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-031 | vppHPFWPResetPushbuttonNative | 1 | 1 | CMD-FWP-HP-RESET | FWP HP | HP FWP reset command interface | COMMAND_INTERFACE | vppHPFWPResetPushbuttonNative | operator/test reset PB | external runtime interface | - | vppHPFWPTripLatchNative | RAW_NODE | PARTIAL | Reset node exists in RAW; exact reset sequencing remains runtime-owned |  | NOT_RUN41 | SOURCE_DEFINED_NOT_RUN41 |  | Reset path exists in source but was not exercised in Run #41. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-032 | vppIPFWPTripPushbuttonNative | 1 | 1 | CMD-FWP-IP-TRIP | FWP IP | IP FWP trip command interface | COMMAND_INTERFACE | vppIPFWPTripPushbuttonNative | operator/test PB writes trip command through runtime interface | external runtime interface | reset PB | vppIPFWPTripCommandNative ¦ vppIPFWPTripLatchNative ¦ vppVCBB01TripCommandNative | RAW_NODE | PARTIAL | All command/latch/breaker nodes exist in RAW; exact client-side sequencing is not re-invented here |  | RUN41_PROVEN | RC_CONFIRMED | ip_bfp | Run #41 ip_bfp passed. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-033 | vppIPFWPResetPushbuttonNative | 1 | 1 | CMD-FWP-IP-RESET | FWP IP | IP FWP reset command interface | COMMAND_INTERFACE | vppIPFWPResetPushbuttonNative | operator/test reset PB | external runtime interface | - | vppIPFWPTripLatchNative | RAW_NODE | PARTIAL | Reset node exists in RAW; exact reset sequencing remains runtime-owned |  | NOT_RUN41 | SOURCE_DEFINED_NOT_RUN41 |  | Reset path exists in source but was not exercised in Run #41. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-034 | vppLPFWPTripPushbuttonNative | 1 | 1 | CMD-FWP-LP-TRIP | FWP LP | LP FWP trip command interface | COMMAND_INTERFACE | vppLPFWPTripPushbuttonNative | operator/test PB writes trip command through runtime interface | external runtime interface | reset PB | vppLPFWPTripCommandNative ¦ vppLPFWPTripLatchNative ¦ vppVCBA02TripCommandNative | RAW_NODE | PARTIAL | All command/latch/breaker nodes exist in RAW; exact client-side sequencing is not re-invented here |  | RUN41_PARTIAL_ELECTRICAL | RC_PARTIAL | lp_bfp | LP electrical trip chain changed, but NRV/drum/common-trip downstream path was not proven before stall. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]
IG-035 | vppLPFWPResetPushbuttonNative | 1 | 1 | CMD-FWP-LP-RESET | FWP LP | LP FWP reset command interface | COMMAND_INTERFACE | vppLPFWPResetPushbuttonNative | operator/test reset PB | external runtime interface | - | vppLPFWPTripLatchNative | RAW_NODE | PARTIAL | Reset node exists in RAW; exact reset sequencing remains runtime-owned |  | NOT_RUN41 | SOURCE_DEFINED_NOT_RUN41 |  | Reset path exists in source but was not exercised in Run #41. | EXACT_RAW_OR_SOURCE_NODE | EXACT_RAW_OR_SOURCE_NODE | PASS_NO_INVENTED_INPUT_NODE | PASS_ALL_INPUTS_LIVE | PASS_ALL_VPP_OUTPUTS_LIVE | Actions #54 / 35309650110 | live census=603; missing_inputs=[]; missing_vpp_outputs=[]

## 02_Input_Groups
input_group_id | input_signature | branch_count | logic_types | rule_ids | logic_names | outputs | systems_or_groups | grouping_policy | run41_group_status | release_status | run41_notes | live_group_status | live_validation_run | live_note
IG-001 | vppGTExhaustMassFlowState | 2 | ALARM | AL-GT-FLOW-L; AL-GT-FLOW-LL | GT exhaust flow low; GT exhaust flow low-low | GT.EXHAUST.FLOW.L; GT.EXHAUST.FLOW.LL | GT Exhaust | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | AL-GT-FLOW-L:RUN41_PROVEN_TRIGGERED; AL-GT-FLOW-LL:RUN41_PROVEN_TRIGGERED | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-002 | vppGTExhaustTemperatureK | 2 | ALARM | AL-GT-TEMP-L; AL-GT-TEMP-LL | GT exhaust temperature low; GT exhaust temperature low-low | GT.EXHAUST.TEMP.L; GT.EXHAUST.TEMP.LL | GT Exhaust | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | AL-GT-TEMP-L:RUN41_PROVEN_TRIGGERED; AL-GT-TEMP-LL:RUN41_PROVEN_TRIGGERED | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-003 | vppHPDrumLevelM | 4 | ALARM | AL-HP-LEVEL-H; AL-HP-LEVEL-HH; AL-HP-LEVEL-L; AL-HP-LEVEL-LL | HP drum level H; HP drum level HH; HP drum level L; HP drum level LL | HRSG.HP.DRUM.LEVEL.H; HRSG.HP.DRUM.LEVEL.HH; HRSG.HP.DRUM.LEVEL.L; HRSG.HP.DRUM.LEVEL.LL | HP Drum | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | AL-HP-LEVEL-H:RUN41_PROVEN_TRIGGERED; AL-HP-LEVEL-HH:RUN41_PROVEN_TRIGGERED; AL-HP-LEVEL-L:RUN41_PROVEN_TRIGGERED; AL-HP-LEVEL-LL:RUN41_PROVEN_TRIGGERED | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-004 | vppHPDrumPressurePa | 2 | ALARM | AL-HP-PRESS-L; AL-HP-PRESS-LL | HP drum pressure L; HP drum pressure LL | HRSG.HP.DRUM.PRESS.L; HRSG.HP.DRUM.PRESS.LL | HP Drum | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | AL-HP-PRESS-L:RUN41_PROVEN_TRIGGERED; AL-HP-PRESS-LL:RUN41_PROVEN_TRIGGERED | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-005 | vppHPTurbineSteamFlowTH | 2 | ALARM | AL-HP-FLOW-L; AL-HP-FLOW-LL | HP turbine steam flow L; HP turbine steam flow LL | HRSG.HP.STEAM.FLOW.L; HRSG.HP.STEAM.FLOW.LL | HP Steam Flow | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | AL-HP-FLOW-L:RUN41_PROVEN_TRIGGERED; AL-HP-FLOW-LL:RUN41_PROVEN_TRIGGERED | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-006 | vppIPDrumLevelM | 4 | ALARM | AL-IP-LEVEL-H; AL-IP-LEVEL-HH; AL-IP-LEVEL-L; AL-IP-LEVEL-LL | IP drum level H; IP drum level HH; IP drum level L; IP drum level LL | HRSG.IP.DRUM.LEVEL.H; HRSG.IP.DRUM.LEVEL.HH; HRSG.IP.DRUM.LEVEL.L; HRSG.IP.DRUM.LEVEL.LL | IP Drum | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | AL-IP-LEVEL-H:RUN41_PROVEN_TRIGGERED; AL-IP-LEVEL-HH:RUN41_PROVEN_TRIGGERED; AL-IP-LEVEL-L:RUN41_PROVEN_TRIGGERED; AL-IP-LEVEL-LL:RUN41_PROVEN_TRIGGERED | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-007 | vppIPDrumPressurePa | 2 | ALARM | AL-IP-PRESS-L; AL-IP-PRESS-LL | IP drum pressure L; IP drum pressure LL | HRSG.IP.DRUM.PRESS.L; HRSG.IP.DRUM.PRESS.LL | IP Drum | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_BOUND_BRANCH_NOT_TRIGGERED | MIXED | AL-IP-PRESS-L:RUN41_PROVEN_TRIGGERED; AL-IP-PRESS-LL:RUN41_BOUND_NOT_TRIGGERED | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-008 | vppIPTurbineSteamFlowTH | 2 | ALARM | AL-IP-FLOW-L; AL-IP-FLOW-LL | IP turbine steam flow L; IP turbine steam flow LL | HRSG.IP.STEAM.FLOW.L; HRSG.IP.STEAM.FLOW.LL | IP Steam Flow | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | AL-IP-FLOW-L:RUN41_PROVEN_TRIGGERED; AL-IP-FLOW-LL:RUN41_PROVEN_TRIGGERED | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-009 | vppLPDrumLevelM | 4 | ALARM | AL-LP-LEVEL-H; AL-LP-LEVEL-HH; AL-LP-LEVEL-L; AL-LP-LEVEL-LL | LP drum level H; LP drum level HH; LP drum level L; LP drum level LL | HRSG.LP.DRUM.LEVEL.H; HRSG.LP.DRUM.LEVEL.HH; HRSG.LP.DRUM.LEVEL.L; HRSG.LP.DRUM.LEVEL.LL | LP Drum | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | AL-LP-LEVEL-H:RUN41_PROVEN_TRIGGERED; AL-LP-LEVEL-HH:RUN41_PROVEN_TRIGGERED; AL-LP-LEVEL-L:RUN41_PROVEN_TRIGGERED; AL-LP-LEVEL-LL:RUN41_PROVEN_TRIGGERED | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-010 | vppLPDrumPressurePa | 2 | ALARM | AL-LP-PRESS-L; AL-LP-PRESS-LL | LP drum pressure L; LP drum pressure LL | HRSG.LP.DRUM.PRESS.L; HRSG.LP.DRUM.PRESS.LL | LP Drum | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_BOUND_BRANCH_NOT_TRIGGERED | MIXED | AL-LP-PRESS-L:RUN41_BOUND_NOT_TRIGGERED; AL-LP-PRESS-LL:RUN41_BOUND_NOT_TRIGGERED | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-011 | vppLPTurbineSteamFlowTH | 2 | ALARM | AL-LP-FLOW-L; AL-LP-FLOW-LL | LP turbine steam flow L; LP turbine steam flow LL | HRSG.LP.STEAM.FLOW.L; HRSG.LP.STEAM.FLOW.LL | LP Steam Flow | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | AL-LP-FLOW-L:RUN41_PROVEN_TRIGGERED; AL-LP-FLOW-LL:RUN41_PROVEN_TRIGGERED | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-012 | vppExternalTripCommandNative | 1 | PROTECTION_CAUSE | PROT-DIRECT-GT | Direct GT trip cause | vppCauseDirectGTTrip | GT Protection | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | PROT-DIRECT-GT:RUN41_PROVEN_ASSERTED | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-013 | vppExternalSTTripCommandNative | 1 | PROTECTION_CAUSE | PROT-DIRECT-ST | Direct ST trip cause | vppCauseDirectSTTrip | ST Protection | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | PROT-DIRECT-ST:RUN41_PROVEN_ASSERTED | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-014 | vppECMS52GTClosedCommandNative ¦ vppGTTripLatchInternal | 1 | PROTECTION_CAUSE | PROT-GT-BRK-OPEN | GT breaker open while running cause | vppCauseGTBreakerOpenWhileRunning | GT Protection | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | PROT-GT-BRK-OPEN:RUN41_PROVEN_ASSERTED | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-015 | vppHPDrumHHRaw | 1 | PROTECTION_CAUSE | PROT-HP-DRUM-HH | HP drum HH protection cause | vppCauseHPDrumHH | HP Drum Protection | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | PROT-HP-DRUM-HH:RUN41_PROVEN_ASSERTED | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-016 | vppHPDrumLLRaw | 1 | PROTECTION_CAUSE | PROT-HP-DRUM-LL | HP drum LL protection cause | vppCauseHPDrumLL | HP Drum Protection | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | PROT-HP-DRUM-LL:RUN41_PROVEN_ASSERTED | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-017 | vppIPDrumHHRaw | 1 | PROTECTION_CAUSE | PROT-IP-DRUM-HH | IP drum HH protection cause | vppCauseIPDrumHH | IP Drum Protection | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | PROT-IP-DRUM-HH:RUN41_PROVEN_ASSERTED | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-018 | vppIPDrumLLRaw | 1 | PROTECTION_CAUSE | PROT-IP-DRUM-LL | IP drum LL protection cause | vppCauseIPDrumLL | IP Drum Protection | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | PROT-IP-DRUM-LL:RUN41_PROVEN_ASSERTED | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-019 | vppLPDrumHHRaw | 1 | PROTECTION_CAUSE | PROT-LP-DRUM-HH | LP drum HH protection cause | vppCauseLPDrumHH | LP Drum Protection | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | PROT-LP-DRUM-HH:RUN41_PROVEN_ASSERTED | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-020 | vppLPDrumLLRaw | 1 | PROTECTION_CAUSE | PROT-LP-DRUM-LL | LP drum LL protection cause | vppCauseLPDrumLL | LP Drum Protection | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | PROT-LP-DRUM-LL:RUN41_PROVEN_ASSERTED | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-021 | vppCauseDirectGTTrip ¦ vppCauseGTBreakerOpenWhileRunning ¦ vppCauseHPDrumLL ¦ vppCauseIPDrumLL ¦ vppCauseLPDrumLL | 1 | TRIP_REQUEST | PROT-GT-REQUEST | GT trip request OR matrix | vppGTTripRequest | GT Protection | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | PROT-GT-REQUEST:RUN41_PROVEN | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-022 | vppCauseDirectGTTrip ¦ vppCauseDirectSTTrip ¦ vppCauseGTBreakerOpenWhileRunning ¦ vppCauseHPDrumHH ¦ vppCauseHPDrumLL ¦ vppCauseIPDrumHH ¦ vppCauseIPDrumLL ¦ vppCauseLPDrumHH ¦ vppCauseLPDrumLL | 1 | TRIP_REQUEST | PROT-ST-REQUEST | ST trip request common-trip matrix | vppSTTripRequest | ST Protection | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | PROT-ST-REQUEST:RUN41_PROVEN | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-023 | vppGTTripRequest ¦ vppGTTripResetNative | 1 | LATCH | PROT-GT-LATCH | GT trip latch | vppGTTripLatch | GT Protection | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | PROT-GT-LATCH:RUN41_PROVEN | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-024 | vppSTTripRequest ¦ vppSTTripResetNative | 1 | LATCH | PROT-ST-LATCH | ST trip latch | vppSTTripLatchPublished | ST Protection | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | PROT-ST-LATCH:RUN41_PROVEN | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-025 | vppGTTripLatch | 1 | BREAKER_SEQUENCE | SEQ-52GT-TRIPCMD | 52GT trip command timing | vpp52GTTripCmd | GT Protection | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | SEQ-52GT-TRIPCMD:RUN41_PROVEN | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-026 | vppECMS52GTClosedCommandNative ¦ vppGTTripLatch | 1 | BREAKER_SEQUENCE | SEQ-52GT-OPEN | 52GT breaker open timing | vpp52GTClosed | GT Protection | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | SEQ-52GT-OPEN:RUN41_PROVEN | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-027 | vppSTTripLatchPublished | 1 | BREAKER_SEQUENCE | SEQ-52ST-TRIPCMD | 52ST trip command | vpp52STTripCmd | ST Protection | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | SEQ-52ST-TRIPCMD:RUN41_PROVEN | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-028 | vppECMS52STClosedCommandNative ¦ vppSTTripLatchPublished | 1 | BREAKER_SEQUENCE | SEQ-52ST-OPEN | 52ST breaker open timing | vpp52STClosed | ST Protection | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | SEQ-52ST-OPEN:RUN41_PROVEN | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-029 | vpp52GTClosed | 2 | PHYSICAL_RESPONSE | RESP-GT-POWER; RESP-GT-SPEED | GT power response after breaker open; GT speed coastdown after breaker open | vppGTGPowerMW; vppGTGSpeedRPM | GT Response | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | RESP-GT-POWER:RUN41_PROVEN; RESP-GT-SPEED:RUN41_PROVEN | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-030 | vppHPFWPTripPushbuttonNative | 1 | COMMAND_INTERFACE | CMD-FWP-HP-TRIP | HP FWP trip command interface | vppHPFWPTripCommandNative ¦ vppHPFWPTripLatchNative ¦ vppVCBA01TripCommandNative | FWP HP | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_HAS_FAILED_BRANCH | RC_NOT_CONFIRMED | CMD-FWP-HP-TRIP:RUN41_FAILED_NOT_PROVEN | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-031 | vppHPFWPResetPushbuttonNative | 1 | COMMAND_INTERFACE | CMD-FWP-HP-RESET | HP FWP reset command interface | vppHPFWPTripLatchNative | FWP HP | Same normalized input-node set => one input group; each rule becomes a branch | NOT_RUN41 | MIXED | CMD-FWP-HP-RESET:NOT_RUN41 | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-032 | vppIPFWPTripPushbuttonNative | 1 | COMMAND_INTERFACE | CMD-FWP-IP-TRIP | IP FWP trip command interface | vppIPFWPTripCommandNative ¦ vppIPFWPTripLatchNative ¦ vppVCBB01TripCommandNative | FWP IP | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_ALL_BRANCHES_PROVEN | RC_CONFIRMED | CMD-FWP-IP-TRIP:RUN41_PROVEN | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-033 | vppIPFWPResetPushbuttonNative | 1 | COMMAND_INTERFACE | CMD-FWP-IP-RESET | IP FWP reset command interface | vppIPFWPTripLatchNative | FWP IP | Same normalized input-node set => one input group; each rule becomes a branch | NOT_RUN41 | MIXED | CMD-FWP-IP-RESET:NOT_RUN41 | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-034 | vppLPFWPTripPushbuttonNative | 1 | COMMAND_INTERFACE | CMD-FWP-LP-TRIP | LP FWP trip command interface | vppLPFWPTripCommandNative ¦ vppLPFWPTripLatchNative ¦ vppVCBA02TripCommandNative | FWP LP | Same normalized input-node set => one input group; each rule becomes a branch | RUN41_HAS_PARTIAL_BRANCH | RC_PARTIAL | CMD-FWP-LP-TRIP:RUN41_PARTIAL_ELECTRICAL | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]
IG-035 | vppLPFWPResetPushbuttonNative | 1 | COMMAND_INTERFACE | CMD-FWP-LP-RESET | LP FWP reset command interface | vppLPFWPTripLatchNative | FWP LP | Same normalized input-node set => one input group; each rule becomes a branch | NOT_RUN41 | MIXED | CMD-FWP-LP-RESET:NOT_RUN41 | PASS_LIVE_INPUT_GROUP | Actions #54 / 35309650110 | missing=[]

## 05_Tag_Identity_Policy
policy | value | meaning
Authoritative source identity | raw_tag_id / opcua_browse_name | Only exact source IDs prove node existence.
Logic inputs | EXACT_RAW_OR_SOURCE_NODE | No fuzzy or semantic substitution.
Derived alarm outputs | TRIPLENS_DERIVED_OUTPUT_NOT_OPCUA | Valid logic result but not a source OPC UA node.
Local display aliases | DISPLAY_ONLY | Never use as proof that a source tag exists.
Scenario Lab-only nodes | EXCLUDED_FROM_OPERATIONAL_LOGIC | May generate incidents but cannot define the analyzer answer.

## 06_Model_Source_Observed
rule_id | group | logic_name | logic_type | input_nodes | condition | delay | reset_hysteresis | output_nodes_or_tags | output_class | raw_inputs_exist | raw_outputs_exist | validation_status | source_basis | notes | input_group_id | input_signature | branch_count | branch_index | run41_status | release_status | run41_evidence_scenarios | run41_evidence_note | input_identity_status | output_identity_status | hallucination_audit_status | live_input_status | live_output_status | live_validation_run | live_validation_note | source_kind | runtime_inclusion | model_source_status | raw_session_status | raw_session_id | raw_session_sha256 | raw_rows | raw_closed_samples | raw_open_samples | open_behavior_test_status | model_package | model_package_sha256 | model_file | model_file_sha256 | model_line_range | source_equation
RESP-ST-GRID-POWER | ST Protection | ST grid power response after 52ST opens | PHYSICAL_RESPONSE | vppSTGeneratorPowerMW ¦ vpp52STClosed | vppSTGridPowerMW = if not vpp52STClosed then 0 else vppSTGeneratorPowerMW | immediate model relation | follows 52ST closed feedback | vppSTGridPowerMW | RAW_NODE | Y | Y | PARTIAL | Model source modelica/TripLens_CombinedCycle_TripTAC_ProcessView_v36.mo lines 1136-1137 (cd454995656af9a8747efe8930d2aa0b92f98e1083acadc858eaa7959ea6d2c5); RAW RAW_SESSION_20260924_191347.csv (055f8a21b8f586feafaa6fe6705cfca05b4f1e833713991a0cac1f0e94ad6fd9). | PHYSICAL_RESPONSE source mapping only. RAW has 282 rows with 52ST closed and 0 open; 52ST OPEN remains NOT_TESTED. | IG-036 | vpp52STClosed ¦ vppSTGeneratorPowerMW | 1 | 1 | NOT_IN_RUN41 | SOURCE_MAPPED_ONLY |  | Confirmed from user-provided model source and later RAW session; not a historical census record. | MODEL_SOURCE_RAW_OBSERVED | MODEL_SOURCE_RAW_OBSERVED | PASS_NO_INVENTED_INPUT_NODE | NOT_PROMOTED_TO_LIVE_RULE | NOT_PROMOTED_TO_LIVE_RULE | NOT_RUN | Model source confirmed; RAW observed closed only (282/282); OPC UA identity not captured; OPEN behavior NOT_TESTED. | MODEL_SOURCE_RAW_OBSERVED | SEARCH_ONLY | MODEL_SOURCE_CONFIRMED | RAW_SESSION_OBSERVED_CLOSED_ONLY | SESSION_20260924_191347 | 055f8a21b8f586feafaa6fe6705cfca05b4f1e833713991a0cac1f0e94ad6fd9 | 282 | 282 | 0 | NOT_TESTED | TripLens_PlantControlV2_ST_GRID_LAYOUT_20260924_ALARM_DISPLAY_ONLY_BUNDLE(2).zip | 6c616330ad80e4b5aad377fd5c4875a2aba7fb15d2366bb1a239eb6dd92231c4 | modelica/TripLens_CombinedCycle_TripTAC_ProcessView_v36.mo | cd454995656af9a8747efe8930d2aa0b92f98e1083acadc858eaa7959ea6d2c5 | 1136-1137 | vppSTGridPowerMW = if not vpp52STClosed then 0 else vppSTGeneratorPowerMW;